## BOQ DG SET
VIDYUTSALLAGAR PVT LTD
ELECTRICAL CONSULTANT AND ENGINEER
SAVITRI, 113, VINAYAK SOCIETY, SAHAKAR NAGAR NO. 1, PUNE 9.
Email: vidyutsallagar@gmail.com
PHONE 24224534
| BOQ FOR DG SET SUPPLY AND ERECTION AND COMMISSIONING | [6 empty] | DATE :- 30 NOV 2022
SMSSRN HOSPITAL NEW BUILDING SOLAPUR
0
SR. | PARTICULARS | QTY | UNIT | MATERIAL RATE | MATERIAL AMOUNT | ERECTION RATE | ERECTION AMOUNT | TOTAL AMOUNT
A | DG SET
1 | 1010 KVA DG SET | 1 | SETS |  | 0 |  | 0 | 0
Supply, Installation, Testing and Commissioning of CPCB2-II APPROVED factory assembled and factory tested, Fuel injected and turbo charged after cooled , prime rated diesel engine alternator set capable of generating full load of 1010 KVA capacity at 50° C, power factor not less than 0.8 lag, 415 Volts, 1500 rpm, 3 phase, 50 Hz, AC supply and driven with diesel engine complete with all accessories such as Base frame, residential silencer, radiator, alternator capable of delivering 415 Volts, 50Hz, 3 phase, PF 0.8, 1010 KVA load, coupling arrangement of alternator with engine, coupling guard, water pump, oil pump, fuel filter, oil filter, air filter, exhaust flexible piping, battery 24 Volts and 180/200 AH capacity (Or suitable as per OEM requirement), battery charging alternator, engine control panel, anti-vibration spring type mounting, statutory permissions, etc. should be included in cost
Exhaust Pipe to have insulation and aluminium cladding. Provision for sampling point for flue gas as per pollution control board norms, with ladder arrangement to reach to sampling point.
Mechanical fuel level indicator with ‘Low’ and ‘High’ markings shall be provided on tank as well as on DG SYNCH panel with Alarm for fuel level “low” ( if fuel level falls below 200ltrs.)
Emergency Push Button with Key: For full cut off the system
DG set should have auto load changeover and suitable for auto load sharing facility.
DG set controller provided with RS 485 port with Register address for DG set load details and load sharing details, for third party Equipment.
First fill (complete) of oils and fuels(Diesel) , charging of battery etc. should be included
DG SET COST SHOULD INCLUDE DG INTERNAL DAY TANK. THERE WILL NOT BE ANY EXTERNAL DAY TANK
2 | Exhaust system
| 20 Meter - EXHAUST PIPING WITH REQUIRED ALL STAND ALONE STRUCTURE & FOUNDATION FOR 1000 KVA DG SET. Exhaust Pipe to have insulation and aluminium cladding. Provision for sampling point for flue gas as per pollution control board norms, with ladder arrangement to reach to sampling point. | 1 | JOB |  | 0 |  | 0 | 0
Note:
a | Class-B MS pipe suitable for DG set exhaust cladded with 50mm thick Glass wool insulation covered with 24SWG Aluminium sheet and provided with rain cap etc., as per specification inclusive of all supports of wall, ceiling, etc.,
b | supporting stack for Exhaust pipes suitable for 1 nos of 1010 kVA of 20 mtr
c | The system shall comply with the statutory norms by MPCB/CPCB.
d | 6 mm thick MS pipes as per IS 3589 shall be supplied. The exhaust system including the silencer must be sized to ensure that back pressure on system does not exceed the back pressure recommended by engine manufacturer. Design calculation in support shall be submitted for approval on award of contract.
e | Pipe shall be thoroughly cleaned of rust and painted with heat resistant paint after fabrication and erection.
f | Exhaust piping and silencer shall be thermally insulated and clad with aluminium sheet.
g | Silencers and Horizontal runs shall be supported on spring supports fixed to ceiling. Vertical runs to have expansion bellows where length exceeds 25 M.
h | Flexible expansion joint of multiple corrugated stainless steel shall be provided between engine exhaust manifold and exhaust piping.
i | Weather cowl at the top are to be provided. aviation lights are to be provided
3 | Supply, laying, testing and commissioning of following sizes of 1100 Volts Copper XLPE Armoured outer FRLS sheath Control Cables
a) | Supply, laying & commsioning of 14 C X 2.5 sq. mm LT XLPE CU Control cable, for control logic between Main LT Panel TO DG AMF controller | 70 | MTRS. |  | 0 |  | 0 | 0
b) | Supply, laying & commsioning of 4 C X 2.5 sq. mm LT XLPE CU Arm cable, for control logic between Main LT Panel TO DG AMF controller | 70 | MTRS. |  | 0 |  | 0 | 0
4 | End Terminations for above sizes of Copper Armoured Control Cables with all required accessories
a) | Supply, laying & commsioning of 14 C X 2.5 sq. mm LT XLPE CU Control cable, for control logic between Main LT Panel TO DG AMF controller | 4 | NOS |  | 0 |  | 0 | 0
b) | Supply, laying & commsioning of 4 C X 2.5 sq. mm LT XLPE CU Arm cable, for control logic between Main LT Panel TO DG AMF controller | 4 | NOS |  | 0 |  | 0 | 0
| TOTAL OF SECTION A |  |  |  | 0 |  | 0 | 0
B | SYNCHRONISATION PANEL
Supply, Unloading, Installation, testing & commsioning of Following Panels. Panels shall be fabricated out of 16/14 swg CRCA sheet steel, with necessory structural supports in form of structural steel sections. Panels shall be floor mounted. The panel shall be compartmental type with suitable size of bus bar and separate cable and busbarchambers. The cable chambers shall be free from any live open connections. Multifuction meters for all incoming feeders. Indication lamps for all incoming and outgoing feeders for phase identifications and for indication of Switch status. (All panels shall comply to IEC 61439-1-2.) All panels switchgear will be provided with lockout tagout (loto)arrangement. Protections: Surge protection on Incomer.Single phasing preventer on incoming bus for phase in balance and single phase preventions.
1 | 1010kVA and 500 kVA (exisiting) DG SET SYNCHRONISATION PANEL | 1 | Nos |  | 0 |  | 0 | 0
All panels Switchgear will be provided with lockout tagout (LOTO)arrangement.
INDICATIONS POSITION
FOR ALL INCOMERS PHASE INDICATION WITH SWITCH POSITION.
FOR ALL OUTGOINGS FOR SWITCH ON OFF & TRIP INDICATION
ALL ACBS WITH - PHASE INDICATION WITH SWITCH POSITION.
PROTECTIONS: SURGE PROTECTION ON INCOMER
SINGLE PHASING PREVENTER ON INCOMING BUS FOR PHASE IN BALANCE AND SINGLE PHASE PREVENTIONS
ALL INCOMERS METER SHALL BE :- SCHNEIDER :- PM- 2230 Series Or Equivalent
ALL OUTGOING METER SHALL BE :- SCHNEIDER :- EM- 6400 NG Series Or Equivalent
ALL METERS SHALL BE COMMUNICATION CAPABLE
REPUTED MAKE SYNCHRONISATION RELAY.
PANEL SHALL BE INDOOR TYPE- IP-43
FORM 3B
ALUMINIUM BUS
FAULT CURRENT :- 40 KA
INCOMING
DG SET NO.1 (500kVA) OUTGOING 800 A FP EDO ACB 40 kA µP LSIGN
DG SET NO.2 (1010kVA) OUTGOING 1600 A FP EDO ACB 40 kA µP LSIGN
OUT GOING
SYNC OUT FOR 630 KVA SOURCES OUTGOING 800 A TP EDO ACB 40 kA µP LSI
SYNC OUT FOR 1000 KVA SOURCES OUTGOING 1600 A TP EDO ACB 40 kA µP LSI
| TOTAL OF SECTION B |  |  |  | 0 |  | 0 | 0
SUMMARY OF LT WORK
A | DG SET |  |  |  | 0 |  | 0 | 0
B | SYNCHRONISATION PANEL |  |  |  | 0 |  | 0 | 0
| TOTAL |  |  |  | 0 |  | 0 | 0