TENDER DOCUMENT

FOR

SUPPLY, INSTALLATION, TESTING & COMMSIONING OF

1000 kVA TRANSFORMER WITH OLTC

PROJECT: - Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

CLIENT: -M/s Shri Markendey Solapur Sahakari Rugnalaya

& Research Center Niyamit.

ARCHITECTS

ARCHITECTS UNITED

- 111/9, 14th Lane Prabhat Road

- Pune – 411004

- Phone: +91 20 25441426 / 25469176

- www.architectsunited.co.in

- VIDYUTSALLAGAR PVT. LTD.

- Electrical Consultant & Engineers

- Savitri, 113, Vinayak Society, Sahakar Nagar No. 1, Pune 9.

- vidyutsallagar.anup@gmail.com;

020-24224534, 9372465729

Project information: - 	M/s Shri Markendey Solapur Sahakari Rugnalaya Niyamit on F.P. No. 19/2, Pachha Peth,Solapur 413005.

Name of work: - 	Supply of Oil immersed, Oil Natural Air Natural (ONAN) outdoor type, three phase, 50 Hz, 1000 kVA 11 kV/433 V with On Load Tap Changer (OLTC) and Remote Tap Change Control (R.T.C.C.) panel for their proposed hospital at Solapur, Maharashtra.

Purchaser/ owner: - 	M/S. Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit

Architect: -			ARCHITECTS UNITED

111/9, 14th Lane Prabhat Road

Pune – 411004

Phone: +91 20 25441426 / 25469176

www.architectsunited.co.in

Electrical consultant: -	VIDYUTSALLAGAR PVT LTD

ELECTRICAL CONSULTANT & ENGINEERS

SAVITRI, 113, VINAYAK SOCIETY,

SAHAKAR NAGAR NO. 1, PUNE 9.

Site conditions: -		Design ambient temperature

Maximum 	45º C

Minimum	14º C

Relative humidity: 50 % RH

Altitude above mean sea level: 457 feet

Installation: Indoor

DISTRIBUTION TRANSFORMER

Scope includes

- Completeness of the equipment shall be the responsibility of the supplier. Any equipment, fittings, and accessories which may not be specifically mentioned in the specification or drawings, but which are usual or necessary for the satisfactory functioning of equipment (successful operation and functioning of the equipment being supplier’s responsibility) shall be provided.

- Specifically it is a turnkey contract with sets handed over to direct use.

- All fitting and accessories or apparatus which may have not been specifically mentioned below, which are necessary and essential for the efficient working of the equipment, shall be deemed to be included in the scope.

- Transportation of transformer & its accessories at Employer’s store at site should be part of scope.

- Packing of the Equipments suitable for (all) weather conditions for proper protection.

- Supervision of unloading of the transformer is also to be considered in the scope.

- Arranging to repair and/or re-order all damaged and short supply items.

- Installation of transformer at site will be done by electrical contractor.

- Supervision from transformer vendor at the time of Final check-up, testing and commissioning in presence of Employer’s representative.

- Transformer and OLTC oil in full capacity as mentioned in GTP/ name plate / technical specification.

This specification covers the requirements at distribution transformer and related equipment accessories. The design, manufacture and performance of equipment shall comply with all applicable standards & regulations and safety codes in the project area. Nothing in this specification shall construe to relieve VENDOR of such responsibility.

Standards:

The equipments covered under this specification shall conform to the latest revisions of relevant Indian Standards some of which are listed below.

- IS 1180	-LEVEL-2

Amendment No.4      	Distribution Transformer

- IS: 10028 		     	Code of practice for installation and maintenance of transformers

- IS: 335				New insulating oil for transformers and switchgears

- IS : 8468-1977			On load tap changers

- IS: 3637 – 1966		Specification for gas operated relays (Buchholz's).

- IS: 10561-1983		Application guide for TRANSFORMER.

General Requirement and Selection of Components:

All material used shall be of best quality and class suitable for working under conditions specified like temperature, overloads, short-circuits, without distortion or deterioration in performance. The exterior of the tank and other steel surfaces exposed to weather shall be thoroughly cleaned and shall have priming of zinc chromate applied. The tank shall be painted with 2 coats of oil and weather resistant, non-fading colour of approved shed. Interior or tank shall be finished with oil insoluble paint.

Steel bolts, nuts and other hardware shall be as per IS-1180 LEVEL-2 Amendment No.4.

The magnetic circuit shall be constructed from high grade cold rolled non-aging grain oriented, silicon steel laminated core. The insulation coat from core to bolt and core to clamp plate shall be suitable to withstand voltage up to 2000V for one minute. The core shall be clamped properly with steel sections & bolts to withstand the mechanical forces during fault.

Windings shall be copper only unless specifically asked for or approved by purchaser.

The winding shall be subjected to shrinking and seasoning so that no further shrinking takes place during service. The core and winding assembly shall be vacuum dried and impregnated with oil immediately.

Connecting strips in the disconnecting chamber shall be easily approachable for disconnection.

The neutral i.e. Star point shall be brought out to a separately, arrangement shall be made for connecting 75 x 10 mm GI earth strip connection to star point earth connection.

The framework, Core clamps and winding clamps shall be securely connected to tank by copper strip.

The transformer shall be designed for minimum losses particularly, No load losses. As per latest ECBC Norms, losses at 50% load and at 100% load shall be guaranteed without tolerance. The bids shall be evaluated considering losses. In case the losses are found excess at the time of testing, related correction shall be done by the manufacturer at his cost.

TRANSFORMER SPECIFICATIONS:

| SR. NO. | TECHNICAL PARTICULARS |  |
| --- | --- | --- |
| 1 | RATING | 1000 KVA OUTDOOR TYPE |
| 2 | NO LOAD VOLTAGE RATIO | 11 kV- 433 V |
| 3 | FREQUENCY | 50 HZ |
| 4 | PHASE | 3 PHASES |
| 5 | VECTOR GROUP | DYN11 |
| 6 | % IMPEDANCE | AS PER IS 1180 LEVEL II Amendment No.4 |
| 7 | TEMPERATURE RISE (OIL / WDG) | 50 / 55 º C |
| 8 | COOLING | ONAN |
| 9 | RELATIVE HUMIDITY | 100 % |
| 10 | TYPE OF TAP CHANGER | ON LOAD TAP CHANGER WITH RTCC |
| 11 | TAPPING RANGE ON HV SIDE | +7.5 % TO -12.5 % IN STEPS OF 1.25% IN 16 STEPS AND 17 POSITIONS |
| 12 | TERMINATION |  |
| 12.A | HV SIDE | CABLE BOX |
| 12.B | LV SIDE | CABLE TERMINATION BOX |
| 13 | HV LV BOX ORIENTATION | 180° |
| 14 | WHEELS | PLAIN BIDIRECTIONAL |
| 15 | DIAL TYPE OIL TEMP. INDICATOR WITH CONTACT | REQUIRED |
| 16 | MAGNETIC OIL LEVEL INDICATOR. | REQUIRED |
| 17 | BUCHOLZ RELAY | REQUIRED |
| 18 | WINDING TEMP INDICATORS | REQUIRED |
| 19 | SUITABLE MARSHALING BOX | REQUIRED |
| S | LOSSES | TO BE FURNISHED BY BIDDER LOSSES SHALL BE AS PER IS-1180 LEVEL – 2 Amendment No.4 NORMS & WILL BE TAKEN IN TO ACCOUNT FOR BID EVALUATION. |

VOLTAGE AND FREQUENCY VARIATIONS:

Transformer shall operate without injurious heating on any Tap under the following conditions provided increase in voltage is not accompanied by reduction in frequency.

- At rated MVA at any voltage within ±10% of the rated voltage.

- At rated current at a voltage equal to 105% of the rated voltage.

- To deliver rated current fewer than 10% continuous over fluxing.

OVERLOADS:

It shall be possible to operate the transformer satisfactorily up to overloads of 150% of the rated value in conformation with the loading guide specified in IS: 2026. There shall be no limitation imposed by bushings, tap changers, auxiliary equipments to meet this requirement.

RATED POWER AND TEMPERATURE RISE:

The transformer shall be capable of operating at rated power specified in the technical schedule on a continuous basis and with the cooling classification given at the most onerous simultaneous climatic conditions specified. The temperature rise specified shall not be exceeded when the transformer is operated continuously at the rated power at the design ambient temperature of 50° C.

RATED VOLTAGE AND TAPPING:

The principal tapping rated voltage shall be as specified. The tapings shall provide a variation in the transformation ratio without producing phase displacement. All tapings shall be full power tapings.

SHORT CIRCUIT WITHSTAND CAPABILITY:

The transformer shall be designed and constructed to withstand without damage to the thermal and dynamic effects of external short circuits between phases or between phase and ground.

RADIO INTERFERENCE:

The transformer shall be designed and constructed so as not to cause any undesirable interference in radio or communication circuits.

TRANSFORMER OIL:

Insulating oil shall be non-PCB oil and conform to IS 335 and shall be suitable in all respects for operating the transformer at the ratings and under conditions laid down in the specification. 10 % extra oil in a non-returnable drum to be supplied along with main equipment.

TAP CHANGING DEVICE:

Transformer is provided with voltage controlling devices such as OLTC (on Load Tap changing gear), RTCC (Remote tap changing gear panel) and standard RTCC panel showing alarms for any of the transformer fault. These would be in the control and relay panel on the 11 kV side of the substation and wired to the transformer through control cables. The control and relay panel would be provided with numerical type relays and annunciating windows to indicate faults on 11 kV equipment. Tap changing device shall be provided on H.V side, circuit type, externally hand operated with necessary indications for tap position and locking arrangement at any of the tapping positions. It shall be designed for bi-directional operation and shall be of self-positioning type and shall have the ± 1.25 % steps

EXPLOSION VENT:

Explosion vent or pressure relief device shall be provided of sufficient size for rapid release of any pressure that may be generated within the tank, and which might result in damage to the equipment. The device shall operate at a static pressure less than the hydraulic test pressure for transformer tank. Means shall be provided to prevent the ingress of moisture and of such a design to prevent gas accumulation.

RATING & DIAGRAM PLATES:

A rating plate of weatherproof material bearing the data specified in the appropriate clauses of IS: 2026/1977. A diagram plate showing the internal connection and the voltage vector relationship of the several windings in accordance with IS: 2026-1977 and a plan view of the transformer giving the correct physical relationship of the terminals.

JOINTS & GASKETS:

All gaskets used for making oil tight joints shall be of proven material such as granulated cork bonded with synthetic rubber gaskets or synthetic rubber or such other good material.

VOLTAGE RATIO:

Unless otherwise specified, the transformer shall be suitable for a voltage ratio of 11 kV/433 V.

VECTOR GROUP:

In case of step-down transformers, the winding connections shall conform to vector group DYN11 unless otherwise specified.

LIST OF FITTINGS:

- Rating and Diagram Plate

- Lifting Lugs, Jacking Pads

- Air Release Plug

- Single Partition conservator with oil filling hole & drain plug

- Explosion vent

- Bottom Drain cum filter valve

- Top filter valve

- Plain oil level gauge

- 2 Nos. Earthing Terminals

- Silica gel breather

- Detachable type radiators

- 4 Nos. Bi-directional flat rollers

- Buchholz relay with one no. alarm and one no. trip contact

- 6” Dial type oil temperature indicators with one no. alarm and one no. trip contact

- 6” Dial type winding temperature indicators with alarm and trip contact

- Magnetic oil level gauge with low level alarm contact

- Marshalling Box

- First fill of oil

- Paint:  Epoxy shade 632 of IS 5

- C.T.’s For Restricted earth fault protection on Transformer.

DRAWINGS AND MANUAL:

The following drawings and manual shall be submitted for the approvals

- General arrangement and dimensional Drawing showing Constructional features and positions of various fittings and Accessories

- General Arrangement Drawing of Marshalling Box.

- Wiring Diagram of Marshalling Box.

- Name plated drawing with Terminal Marking and connection Diagrams.

- Routine Test Certificates.

- Wiring diagram

- Foundation drawing.

TESTS:

All routine and type tests and type tests asked for shall be carried out by vendor in presence of representative of owner and consultant. Following tests shall be carried out on all transformers and shall be included in the quotation.

- Measurement of winding resistance.

- Ratio, polarity and phase relationship.

- Impedance voltage

- Load losses.

- No-load losses and No-load current.

- Insulation resistance.

- Induced over voltage withstand.

- Separate source voltages withstand.

- Duty cycle of On-load Tap Changer.

- All the routine tests shall be conducted in the suppliers' laboratory at their cost.

REJECTION:

The Transformer can be rejected if during testing following condition arise.

- No load losses exceed guaranteed value by 10%.

- Load losses exceed guaranteed value by 10% However; losses shall not exceed limits given in ECBC Norms.

- Impedance value differs the guaranteed value by + /- 10% or more.

- Oil or winding temperature rise is more than specified value.

- Total Losses exceed the Max limit indicated by IS-1180 LEVEL 2 Amendment No.4

- Transformer is not manufactured in accordance with specification. PURCHASER Reserves right of retaining the rejected transformer until VENDOR replaces it with new acceptable transformers at no extra cost.

PACKING AND FORWARDING :

SCOPE:
This specification covers equipment /material packing transportation and protection of material during transit and storage.

PACKING:

Vendor shall be responsible for any damage during transit due to improper or insufficient packing. Packing shall be constructed out of sound material and dimensions suitable to the goods, size and weight Fragile material shall be security braced within container or amply fastened to prevent shifting or battering. Cushion lining of appropriate material shall be provided wherever necessary loose material MS parts Nuts bolts etc, shall be packed separately in gunny bags with polythene bags sealed and tagged Components containing glass shall be provided with shock absorbing material cover like thermos Cole. In case of bulk materials Vendor shall supply the same in minimum sub-assemblies within the transport limitation Care shall be taken for preventing any seepage of water in case required to prevent any corrosion during transport. All spare parts shall be separately packed and treated for long storage in site condition. Each crate/package shall contain a packing list in waterproof envelope Vendor/Contractor shall supply any material found short inside the packing at no extra cost. All packing material shall become property of Contractor as the purchaser. All packages shall be clearly, legibly and durably marked on the least two sides. 
Destination address 
Dimension and weight 
Sign showing “Side up “with arrow 
Sign “Fragile and Handle with care” for delicate equipment 
Slinging and sling positions 
Important handling and unpacking instructions

Transport: 
No material shall be dispatched without prior consent shipping clearance by the purchaser/ consultant The vendor shall intimate in advance date of dispatch and probable date of delivery at Site so that unloading arrangements can be made, particularly for heavy material in case any equipment is to be transported in sub-assemblies or parts, vendor shall furnish all particulars and match marking. Such sub-assemblies shall be well within transportation and handling limitations. The transporters shall be provided with proper address and other details, working hours etc. The crate or packages shall be properly secured to avoid movements during transit to minimise possibility of damage.

SCHEDULE OF TECHNICAL PARTICULARS- GTP:

| SR. NO. | PARTICULARS | VENDOR TO DECLARE |
| --- | --- | --- |
| 1 | Rated KVA |  |
| 2 | Winding material (LV/HV) |  |
| 3 | Rated Voltage at No Load for HV |  |
| 4 | Whether transformer is suitable for Indoor /Outdoor installation |  |
| 5 | Taps on HV winding |  |
| 6 | Tapping Mode& Model of tap switch with Make |  |
| 7 | OLTC Model & Make |  |
| 8 | Rated voltage at No Load for LV |  |
| 9 | Rated current at Full Load for HV |  |
| 10 | Rated current at Full Load for LV |  |
| 11 | No. of phases |  |
| 12 | Type sealed / non sealed |  |
| 13 | Type of cooling |  |
| 14 | Vector group |  |
| 15 | Type of Core |  |
| 16 | Core material used & its grade |  |
| 17 | Thickness of core lamination in mm |  |
| 18 | Weight of Core |  |
| 19 | Flux density (Bm) |  |
| 20 | Type of connection for H.V. Winding |  |
| 21 | Conductor size HV |  |
| 22 | Insulation provided to H.V winding. |  |
| 23 | No of HV winding turns |  |
| 24 | No. of HV coils /phase |  |
| 25 | Type of connection for L.V. Winding |  |
| 26 | Conductor size LV (Rect. Strip) |  |
| 27 | Insulation provided to L.V winding. |  |
| 28 | No of LV winding turns |  |
| 29 | No. of conductors in parallel for LV winding |  |
| 30 | Rated frequency |  |
| 31 | Rated temperature rise Oil |  |
| 32 | Rated temperature rise Winding |  |
| 33 | Weight of core and winding |  |
| 34 | Total weight |  |
| 35 | Quantity of Oil |  |
| 36 | Total Losses at 50% Loading |  |
| 37 | Total Losses at 100% loading |  |
| 38 | Tank dimensions inside Length/Width/Height |  |
| 39 | Tank Dimensions overall Length/Width/Height (+/-10% Tol.) |  |
| 40 | Size of Radiators fins |  |
| 41 | No. of Radiators |  |
| 42 | Total no. of Radiators fins |  |
| 43 | Minimum clearance between phase to phase for HV in cable box |  |
| 44 | Minimum clearance between phase to earth for HV in cable box |  |
| 45 | Minimum clearance between phase to phase for LV in cable box |  |
| 46 | Minimum clearance between phase to earth for LV in cable box |  |
| 47 | Efficiency at 75°C at unity P.F. at 125% load |  |
| 48 | Efficiency at 75°C at unity P.F. at 100% load |  |
| 49 | Efficiency at 75°C at unity P.F. at 75% load |  |
| 50 | Efficiency at 75°C at unity P.F. at 50% load |  |
| 51 | Efficiency at 75°C at unity P.F. at 25% load |  |
| 52 | Efficiency at 75°C at 0.8 P.F. at 125% load |  |
| 53 | Efficiency at 75°C at 0.8 P.F. at 100% load |  |
| 54 | Efficiency at 75°C at 0.8 P.F. at 75% load |  |
| 55 | Efficiency at 75°C at 0.8 P.F. at 50% load |  |
| 56 | Efficiency at 75°C at 0.8 P.F. at 25% load |  |
| 57 | Rating of H.V. Bushings ( in KV/A) |  |
| 58 | Rating of L.V. Bushing ( in KV/A) |  |
| 59 | Impedance value at 75°C |  |
| 60 | Separate source power frequency withstand test for HV for 1 minute in KV (min) |  |
| 61 | Separate source power frequency withstand test for LV for 1 minute in KV (min) |  |
| 62 | Induced over voltage withstand test for 1 min. specify voltage frequency, time for test. |  |
| 63 | Impulse test value (in KVp). |  |

PAYMENT TERMS:

| Stage of payment |  | Percentage of Material cost as per order | Percentage of Installation cost as per order. |
| --- | --- | --- | --- |
| Advance |  | 10 % | 0% |
| Against Delivery of material on site. |  | 60% | 0% |
| Against virtual completion |  | 10% | 80% |
| Against Testing |  | 10% | 10% |
| Against total Commissioning |  | 5% | 5% |
| After Defect liability period |  | 5% | 5% |
| Total payment |  | 100% | 100% |

DEVIATIONS FROM TECHNICAL SPECIFICATIONS

All deviations from technical specifications of contract shall be filled in hereby the bidder.

SECTION				CLAUSE NO.			DEVIATION

The bidder hereby certificates that the above mentioned are only deviations from technical Specifications of this enquiry.

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)