## BOQ HT EQUIP CAPITAL GOODS
VIDYUTSALLAGAR PVT LTD
ELECTRICAL CONSULTANT AND ENGINEER
SAVITRI, 113, VINAYAK SOCIETY, SAHAKAR NAGAR NO. 1, PUNE 9.
Email: vidyutsallagar@gmail.com
PHONE 24224534
| BOQ FOR HT EQUIPMENT | [6 empty] | DATE :- 30 NOV 2022
SMSSRN HOSPITAL NEW BUILDING SOLAPUR
0
SR. | PARTICULARS | QTY | UNIT | MATERIAL RATE | MATERIAL AMOUNT | ERECTION RATE | ERECTION AMOUNT | TOTAL AMOUNT
A | HT WORK INSIDE IN OWNER PREMISES
Supply and laying of HT 11 kV XLPE INSULATED cable of 3 core 95 sq.mm.
1 | FROM TAP OFF POINT TO METERING KIOSK ( Round Arm ) | 0 | Mtr. |  | 0 |  | 0 | 0
2 | FROM METERING KIOSK 1 TO METERING KIOSK 2 ( Round Arm ) | 20 | Mtr. |  | 0 |  | 0 | 0
2 | FROM METERING KIOSK 2 TO HT VCB ( Round Arm ) | 20 | Mtr. |  | 0 |  | 0 | 0
3 | FROM HT VCB TO TRANSFORMER ( Round Arm ) | 20 | Mtr. |  | 0 |  | 0 | 0
4 | Supply and fixing of Heat shrinkable Indoor type end termination (Raychem) for 11 KV 3 core 95 sq. mm. XLPE insulated cable used for
4.1 | METERING KIOSK | 4 | Set. |  | 0 |  | 0 | 0
4.2 | HT VCB PANEL | 4 | Set. |  | 0 |  | 0 | 0
4.3 | TRANSFORMER | 1 | Set. |  | 0 |  | 0 | 0
5 | Supply and fixing of Heat shrinkable out door type end termination (Raychem) for 11 KV 3 core 150 sq. mm. XLPE insulated cable used for
5.1 | TAP OFF POINT | 0 | Set. |  | 0 |  | 0 | 0
| TOTAL OF SECTION A |  |  |  | 0 |  | 0 | 0
B | HT SOURCE & EQUIPMENT
1 | Supply, fixing, testing and commissioning of MSEDCL approved 11 KV -Metering kiosk inclusive of following | 1 | Set |  | 0 |  | 0 | 0
A) CT SPECIFICATION (MSEDCL APPROVED) CAST RESIN
Ratio 75/5 Amp or as per MSEDCL STANDARDS/ GUIDELINES
Class 0.2
Burden 10 VA
As per I.S 2705
B) PT SPECIFICATION (MSEDCL APPROVED) CAST RESIN
Ratio 11 KV/Rt 3/110/Rt 3
Class 0.2
Burden 100 VA
As per I.S 3156
Provision for meter compartment in side the kiosk with reading window.
with Digital TOD Trivector meter of MSEDCL approved make.(prevailing).
2 | Supply , Installation of testing and commissioning of 11 KV, 630A , 26.3 KA Indoor type(IP54) compact type VCB at consumer end for transforemr protection with 16 window annunciation panel and (1 in - 2 out)(3 MODULE) | 1 | Set |  | 0 |  | 0 | 0
| TOTAL OF SECTION B |  |  |  | 0 |  | 0 | 0
C | TRANSFORMER
1 | Supply and Installation of 11 KV 1000 kVA 11000/433 V, Copper Coil winding, , delta star connected outdoor type oil cooled ONAN transformer, Vector Group Dyn11, OLTC with Taping on Primary +7.5 % to -12.5% in steps of 1.25% through On Load Tap Changer, Class A Insulation level, boltless core design, in-house core cutting and stamping facility, Efficiency not below 98.5%, , With HV cable End Box and LV cable termination Box, ONAN cooling system & all standard accessories like dial type thermometer, breather, rollers, buchholz relay, Marshalling box for interconnection with incomer switch and hooters, First fill of oil, Rating and diagram Plate, etc. Scope will also consist of Supply & Laying of required control cable set (approx length 20 Mtrs.) Scope will also consist of Filetaration of Transformer oil before commisioning. | 1 | Set |  | 0 |  | 0 | 0
| TOTAL OF SECTION C |  |  |  | 0 |  | 0 | 0
SUMMARY OF LT WORK
A | HT WORK INSIDE IN OWNER PREMISES |  |  |  | 0 |  | 0 | 0
B | HT SOURCE & EQUIPMENT |  |  |  | 0 |  | 0 | 0
C | TRANSFORMER |  |  |  | 0 |  | 0 | 0
| TOTAL |  |  |  | 0 |  | 0 | 0