ELECTRIFICATION WORK

TENDER DOCUMENT

FOR

PROJECT: - Shri Markendey Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

CLIENT: -M/s Shri Markendey Solapur Sahakari Rugnalaya

& Research Center Niyamit.

ARCHITECTS UNITED

- 111/9, 14th Lane Prabhat Road

- Pune – 411004

- Phone: +91 20 25441426 / 25469176

- www.architectsunited.co.in

ELECTRICAL CONSULTANT-

- VIDYUTSALLAGAR PVT. LTD.

- Electrical Consultant& Engineers

- Savitri, 113, Vinayak Society, Sahakar Nagar No. 1, Pune 9.

- vidyutsallagar.anup@gmail.com;

ENQUIRY FOR SUPPLY AND INSTALLATION OF ELECTRIFICATION WORK

From:          ____________________________________,
____________________________________, 
____________________________________, 
____________________________________.

Date:	 ____________________________________.

To,

M/s Shri Markendey  Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

Kind Attn.

Dear Sir / Madam,

Sub: -Supply and Installation, Testing and Commissioning of Electrification work for M/S Shri Markendey Solapur Sahakari Rugnalaya Niyamit, Solapur Maharashtra.

We have pleasure in submitting herewith Tender Quotation for the above-mentioned works, duly completed in all respects.

- We represent that we have the adequate experience and expertise in handling and delivering the Work as envisaged in the Enquiry as above in accordance with the quality and time period desired by you.

- We have read and studied the entire Enquiry Document for the proposed work we agree to abide by them.

- We agree to execute and complete the proposed work at the rates quoted herewith.

- We have inspected the site of works and acquainted ourselves with the local conditions. We will not claim any extra amounts for reasons arising out of site conditions. Rates quoted by us include all such eventualities.

- The rates quoted in the Enquiry shall be valid for three months from the date of opening of the Enquiry.

- The bid document shall be filled properly and all relevant information asked for shall be provided in due format.

- Bidders are requested to give deviations/comments/assumptions/alternatives clearly in deviation pages / separate pages based on their observations.

- Base BOQ shall not be altered. Deviations for technical specifications shall also be clearly given in the bids. Technical specifications for which deviations are not provided with the bids or not accepted during negotiations shall not be revised after order.

- Bidders are requested to specify the makes and catalogue numbers of Light fitting considered.

- I/we understand that you are not bound to accept the lowest or any tender you may receive. This Tender document shall be a part of the Contract.

I/ we do hereby offer to execute the work under the Item rate Contract at the respective rates mentioned in the Schedule of Quantities. Cost of this works out to

Rs………………………………….……………………./-

(Rs.……………………………………………………………………………………………………………….…………………………………………………………. Only)

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)

TENDER DETAILS

- Sealed item rate tenders are invited on behalf of M/S- Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit for Supply and installation, testing and commissioning of Electrification work, as per BOQ, for their proposed Hospital building at SOLAPUR, Maharashtra.

- The purchaser reserves the right to accept any tenders received after the expiry of the time notified.

- The duly completed and signed Tender document in a sealed envelope super-scribed with the name of work and name of the Bidder clearly.

- This should be submitted at the office address mentioned below on dated 25/01/23,   19.00 Hrs.

M/S. Shri Markendey Solapur Sahakari Rugnalaya &

Research Center Niyamit

Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

- The Owners at their sole discretion can accept any Tender or reject all the received Tenders. This note shall form part of the Contract.

- The Tender is an item rate Tender, though the total value of Contract shall appear on the letter of intent or work order, the successful Contractor shall be paid as per measured, erected and certified quantities of ‘Bill of Quantities’ on pro rata basis as per the payment terms.

- Submission of queries related to bid – on dated 21/01/23,   17:00 Hrs.

Please note: - queries raised after dated 21/01/23,   17:00 Hrs.will not be entertained.

- Please submit your queries & soft copy of BOQ on following Email-ids.

vidyutsallagar.anup@gmail.com

vidyutsallagar.mandar@gmail.com

newbuildingmssrn@gmail.com,

tendermssrn@gmail.com,

pranav@architectsunited.co.in

In case, any clarification is required, the Bidders shall obtain the same from the Consultant/Client in writing. All such clarifications shall be binding both on the Purchaser/Consultant and the Bidder.

At any time prior to the deadline for submission of Bids, the Purchaser/Consultant may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, modify the tender document by amendments.

The prices & rates quoted by the Bidder’s shall be valid & shall be kept open for acceptance for a minimum period of ninety ( 90) days from the date of opening of tender.

The acceptance/ rejection of the quotation will rest with the purchaser, who does not bind himself to accept the lowest quotation or any quotation & reserves to himself the full rights for the following without assigning any reason whatsoever.

Whenever it is stated in this contract that such and such a supply is to be effected or such and such a work is to be carried out, or provided it shall be understood that the same shall be effected/carried out by the supplier within the contract price, unless a different intention is specifically and expressly stated herein or otherwise explicit from the context.

Project information: - 	Shri Markendey Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

Name of work: - 	Supply and Installation, Testing and Commissioning of HT/LT Electrification work as per BOQ.

Purchaser/ owner: - 	M/S. Shri Markendey Solapur Sahakari

Rugnalaya & Research Center Niyamit

Architect: -			ARCHITECTS UNITED

111/9, 14th Lane Prabhat Road

Pune – 411004

Phone: +91 20 25441426 / 25469176

www.architectsunited.co.in

Electrical consultant: -	VIDYUTSALLAGAR PVT LTD

ELECTRICAL CONSULTANT & ENGINEERS

SAVITRI, 113, VINAYAK SOCIETY,

SAHAKAR NAGAR NO. 1, PUNE 9.

Site conditions: -		Design ambient temperature

Maximum 	45º C

Minimum	14º C

Relative humidity: 50 % RH

Altitude above mean sea level: 457 feet

Installation: Indoor

TENDER GENERAL, TERMS & CONDITIONS

General requirement

This Section describes the Scope of Works for the Electrification Works for the M/S Solapur Sahakari Rugnalaya Niyamit, Solapur Maharashtra, Proposed hospital building at SOLAPUR.

All the material supplied shall be strictly in adherence to the specifications in this document and the prevailing IS and IEC. The installation of equipment shall conform to the requirement of manufacturer's installation manuals. The Contractor's scope includes performance of all necessary tests (using his own testing apparatus), preparation of all documents/applications for statutory approval and obtaining Statutory Approval for energizing the installation carried out by him .The Tenderer shall furnish all labour, skilled, semi-skilled & unskilled, supervisory and administrative personnel, erection tools & tackles, equipment for testing & commissioning for timely & effective execution of the contract. The contractor shall protect his work, equipment and material from theft or tampering. The contractor shall be fully and finally responsible for proper installation and satisfactory operation of the plant and equipment under his scope of work to the entire satisfaction of the client/PM/consultant. Equipment and material that are wrongly installed shall be removed and reinstalled to comply with the design requirement at the contractor’s expense to the satisfaction of the client/PM/consultant.

The Scope of Works includes all Electrical works outlined in the

- BOQ

- Drawings,

- & technical specifications

Should be executed in accordance with them. And the contractor shall include all the works in this tender quote.

The filled BOQ by contractors should be in the same format as the tender BOQ with no removal or addition of line items or blank rows.

Client shall be allowed to change the scope of the works by removing or adding items. The cost impact such change shall be calculated based on the quoted rates, in the BOQ.

The client shall also free issue some items of equipment. For all “Free Issue” items the contractor is responsible for taking ownership of the item on arrival on site and is responsible for the installation and commissioning of the free issue item.

The tender rate is deemed to have included for all the contractor’s cost and profit associated with “Free Issue items including profit.

The list of equipment which can be removed from contractor’s scope, and supplied as free issue

- DG sets

- Synch Panel

- Transformer

- UPS system

- Light Fittings

There are some items for “RATE ONLY” OR WITH QUANTITY AS ZERO (0). If the rates for such items are not quoted then the rate will be considered as zero (0), and will be used for bill certification.
As a special condition for this project, the electrical power and water required for execution work will have to be arranged by the contractor at his own cost. Client will not make any type of arrangement or provide any type of help in arranging these. Contractor shall take care of these expenses while preparing quotes.

DEFINITIONS AND INTERPRETATION

DEFINITIONS

Unless repugnant to the context or meaning thereof, in this tender document the following shall have the meaning assigned to them below

Authorized Signatory
The Authorized Signatory shall be as specified by the Bidder.  In case the bid is submitted by a single Bidder, the Bidder shall provide a valid Power of Attorney authorizing the Authorized Signatory to submit the bid and represent/negotiate with the CLIENT /ARCHITECTS / ELECTRICAL CONSULTANT.

Applicable Approvals 
The Applicable Approvals means any and all “No Objection Certificates”, approvals, permissions, clearances, licenses, authorizations, consents, no objections like drainage, water, garden from any Government Authority or any Person required in relation with the execution of proposed Agreement between the Company and the Selected Contractor or for undertaking, performing or discharging the obligation contemplated by this tender document or other agreements referred to in this tender document, including payments of any amounts hereunder, under the applicable Law or otherwise in connection with this tender document or other agreements referred to hereunder.
(Note:  To get a list of tentative approvals from a list of authorities)

Bidder 
Bidder refers to the Qualified Bidder/s that is bidding for undertaking the Work.

Company/ Client shall mean M/S Solapur Sahakari Rugnalaya Niyamit, Solapur  Maharashtra.Contractor
The selected Bidder shall mean the Bidder that finally enters into contract with the Company in relation to the Work.

Governmental Authorities
Governmental Authorities shall mean Local Industrial Development Authority, Pollution Control Board, Sub-registrar of assurances, FEDERAL Electrical and Water Authority , and/or any other applicable legislative body, regulatory or administrative authority, agency or commission or any court, board, bureau, instrumentality, tribunal or judicial or arbitral body, having jurisdiction over the territory of INDIA or any part thereof

Law/s 
Laws/s shall mean and include all statutes, enactments, acts of legislature or parliament, laws, ordinances, rules, bye-laws, regulations, notifications, guidelines, policies, directions, directives and orders of any Governmental Authority or court, including any amendments, re-enactment, substitution thereof, and shall include any subordinate legislation, rules and regulations of INDIA, from time to time.

Preferred Bidder
 Preferred Bidder shall mean the Bidder invited by the CLIENT /ARCHITECTS / ELECTRICAL CONSULTANT/PMC for final discussions and for entering into contract(s) for the Work.

Request for Proposal or tender document
Request for Proposal shall mean this invitation to submit technical and financial proposal issued by the CLIENT /ARCHITECTS / ELECTRICAL CONSULTANT/PMC to the Qualified Bidders for selection of the Bidder in relation to the Work.

TENDER Document
TENDER Document shall mean this document including all the documents referred to in this document being issued to the Bidders

Site Address:-

M/S. M/s Shri Markendey Solapur Sahakari Rugnalaya &

Research Center Niyamit

Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

Tender
Tender shall refer to the technical and financial proposals of Bidders in response to this tender document organized in a manner specified herein.   This technical and financial proposal shall include the qualifications of the concerned Bidder/Bidding Consortium.

"Taxes" 
Taxes shall mean any and all applicable tax and taxes (including, but not limited to any Goods & Service Tax(GST), income tax, tax deducted at source, value added tax or sales tax, transfer duties, stamp or other duty, levy, impost, charge, fee, deduction, or withholding of any nature and howsoever called or described) whether imposed by the state or central Government, Governmental Authorities, and/or by whomsoever and where so ever imposed, levied, collected or assessed.

Work
Work shall mean the electrification and cabling of the Hospital building, including any / all infrastructure facilities proposed to be put up for the Hospital at SOLAPUR, INDIA, as indicated by the ARCHITECT / ELECTRICAL CONSULTANT or such other point(s) as may be specified by the ARCHITECT

Interpretation

In the interpretation of this tender document, unless the context otherwise requires: The singular of any defined term includes the plural and vice versa, and any word or expression defined in the singular has the corresponding meaning used in the plural and vice versa.

A reference to any gender includes the other gender

Unless otherwise stated, a reference to a Clause, Sub-Clause, Paragraph, Subparagraph, Annex, Exhibit, Attachment, Schedule or Recital is a reference to a Clause, Sub-Clause, Paragraph, Subparagraph, Annex, Exhibit, Attachment, Schedule or Recital of this tender document

A reference to any agreement is a reference to that agreement and all annexes, attachments, exhibits, schedules, appendices and the like incorporated therein, as the same may be amended, modified, supplemented, waived, varied, added to, substituted, replaced, renewed or extended, from time to time, in accordance with the terms thereof

The terms “include” and “including” shall be deemed to be followed by the words “without limitation”, whether or not so followed

A reference to a “writing” or “written” includes printing, typing, lithography and other means of reproducing words in a visible form

Any date or period set forth in this tender document shall be such date or period as may be extended pursuant to the terms of this tender document. A reference to “month” shall mean a calendar month, and a reference to “day” shall mean a calendar day, unless otherwise specified

The terms "hereof, "herein", "hereto", "hereunder" or similar expressions used in this tender document mean and refer to this tender document and not to any particular Article, Clause or Section of this tender document. The terms "Article", "Clause", “Paragraph” and “Schedule” mean and refer to the Article, Clause, Paragraph and Schedule of this tender document so specified.

And the descriptive headings of Articles and Sections are inserted solely for convenience of reference and are not intended as complete or accurate descriptions of content thereof and shall not be used to interpret the provisions of this tender document.

## CONDITIONS FOR ELECTRIFICATION
The Agreement between the Company and Contractor conveys the final agreement on terms and conditions. In case of any conflicts, the general and special terms, conditions and specifications, drawings furnished by the Company/ ARCHITECT / ELECTRICAL CONSULTANT on behalf of the Company from time to time will be treated as final.

This Tender document does not purport to contain all the information that each Bidder may require and accordingly is not intended to form the basis of any investment decision or any other decision to participate in the bidding process for the selection of the contractor for the proposed Work (as defined hereafter) on behalf of M/S Shri Markendey Solapur Sahakari Rugnalaya Niyamit, Solapur Maharashtra. Each Bidder should conduct its own investigations and analysis and check the accuracy, reliability and completeness of the information in this document and obtain independent advice from appropriate sources.

This Tender document includes certain statements, estimates and projections with respect to the anticipated future performance of the Work. Such statements, estimates and projections reflect various assumptions concerning anticipated results, which assumptions may or may not prove to be correct. Neither the Company, nor the ARCHITECT/ELECTRICAL CONSULTANT, make any representation or warranty with respect to the accuracy of such statements, estimates and projections and actual performance of the Work or any opportunity that may be materially different from that set forth in such statements, estimates and projections.

The information provided in this tender document is based on the facts, information and assumptions holding well as on the date of issue of the tender document.  Bidders may please note that this is subject to changes in the future, and the CLIENT /ARCHITECTS / ELECTRICAL CONSULTANT/PMC will inform the Bidders of material changes, if any, prior to submission of bids.

Neither the Company nor the ARCHITECTS / ELECTRICAL CONSULTANT/PMC or their respective employees or consultants shall be liable to any Bidder or any other Person under any Law including the law of contract, tort, the principles of restitution or unjust enrichment or otherwise for any loss, expense or damage which may arise, or be incurred, or suffered, in connection with this TENDER Document, or any matter that may be deemed to form part of this TENDER Document, or the award of the contract, or any other information supplied by or on behalf of the Company or the ARCHITECT / ELECTRICAL CONSULTANT or their respective employees or consultants or otherwise arising in any way from the selection process for the award of the contract for the Work.

If any discrepancy is noticed by any Bidder in this TENDER Document, it must be intimated immediately to the ARCHITECT / ELECTRICAL CONSULTANT or at the address mentioned below. If no intimation is received by ARCHITECT / ELECTRICAL CONSULTANT at the below mentioned office within 21 days from the date of issue of this TENDER Document, then it shall be deemed that the TENDER Document received by the Bidder is complete in all respects and that the Bidder is satisfied that the TENDER Document is complete.

No extension of time will be granted under any circumstances to any Bidder for submission of its bid on the grounds that the Bidder did not obtain a complete set of the tender document.

The ARCHITECT / ELECTRICAL CONSULTANT is not bound to accept any or all the Proposals. The ARCHITECT / ELECTRICAL CONSULTANT reserves the right to reject any or all the Proposals without assigning any reasons. No Bidder shall have any cause for action or claim against the ARCHITECT / ELECTRICAL CONSULTANT or the Company or any of their respective officers, employees, consultants, successors or assignees for rejection of his bid.

Failure to provide information that is essential to evaluate the Bidder’s qualifications or to provide timely clarification or substantiation of the information supplied, may result in disqualification of the Bidder.

This TENDER Document and the information contained herein are strictly confidential and are for the use of only the Person(s) to whom it is issued. It may not be copied or distributed by the recipient to third parties (other than in confidence to the recipient’s professional advisors).

MODIFICATION AND VARIATION: 
This Agreement may be amended, modified or cancelled, only in writing by the Company and the Contractor, or their duly Authorised Representatives. 
Since the Company is desirous that the supply of material be at subsidised rates, Bidders are requested to quote the cost of supply of each item and erection of each item separately. In case of such supplies, the Contractor will be paid for only erection work.

MATERIALS AND SERVICES:

The Contractor shall provide at his cost all material, tools, tackles, skilled manpower for proper execution of Works specified in the schedule of quantities and as per drawings and specifications. Any discrepancies in schedule of quantities and drawings shall be brought to notice of engineer / ARCHITECT / ELECTRICAL CONSULTANT /PMC /Company for decisions.

MATERIAL AND WORKMANSHIP:
All the materials to be supplied for execution of shall be of first quality, new and strictly as per specifications.
All the work shall be executed with highest workmanship, and as directed by ARCHITECT / ELECTRICAL CONSULTANT /Company / PMC.
In case of non-availability of any approved material, approval for alternative make shall be taken from ARCHITECT / ELECTRICAL CONSULTANT and the Company prior to using such material.
The Contractor shall employ no child labour.
It is binding on Contractor to take all safety precautions at the time of execution of the Works.

LABOUR AND INSURANCE
Contractor shall be responsible for injury to person animal or things, for all damages caused to property from operations or negligence of himself or his employees/subcontractors. The contractor shall indemnify owner / Engineer and their employees and hold them harmless in respect of any and all expenses arising from such injury or damage and claims arising thereof. The damages to the property, plant and equipment caused due to such negligence shall be made good by the contractor at his own cost to the satisfaction of the owner / engineer within a specific time. The owner in concurrence with engineer shall be entitled to deduct amount of damage, compensation for loss arising from such damages/injuries/accidents in case of default. All laws related to PF, ESI, Medical insurance etc. shall be adhered to by the contractor. No child labour shall be employed by contractor.

INSURANCE:

Contractor shall insure all the equipment and work in his scope including necessary transit insurance.

Insurance against injury to Person and Property Without prejudice to his liability to indemnify the Owner under Clause 45 of these conditions, the Contractor shall maintain and shall cause any Sub-Contractor to maintain: A. Such insurances as are necessary to cover the liability of the Contractor or as the case may be such Sub-Contractor, in respect of personal injuries or deaths arising out of or in the course of or caused by the carrying out of the work, and B. Such insurances as may be specifically required by the Contract Bills in respect of injury or damage to property real or personal arising out of or in the course of or by reason or the carrying out of the work, and caused by any negligence, omission or default of the Contractor, his servants or agents or, as the case may be of such Subcontractors, his servants or agents. The Contractor shall produce or cause any Sub-Contractor to produce for inspection the relevant policy or policies of insurance together with the receipts in respect of premiums paid under such policy or policies as and when required so to do by the Architect provided always that as and when may be reasonably required by the Architect the production by either the Contractor or any Sub-Contractor of a current certificate of insurance from the company or firm which shall have issued the policy or policies afore side shall be a good discharge of the Contractor’s obligation to produce or to cause the production of the policy or policies and the receipts in respect of premium paid. The Contractor shall maintain in the joint names of the Owner and Contractor such insurances as may be required in respect of any expenses, liability, loss, claim or proceedings which the Owner may incur or sustain reason of injury or damage to property real or personal arising out of or in the course of or by reason of the carrying out of the work, and caused otherwise than by the negligence, omission or default of the Contractor , his servants or agents or any Sub-Contractor, his servants or agents. Any such insurance as is referred to in the immediately preceding paragraph shall be placed with insurers to be approved by the Architect and the Contractor shall have to deposit with him the policy or policies and the receipts in respect of premiums paid. Should the Contractor or any Sub-Contractor make default in continuing to insure as providing in sub-clauses (1) and (2) if this condition the Owner may himself insure against any risk with respect to which the default shall have occurred and may deduct a sum equivalent to the amount paid in respect of premiums from any monies due to or become due to the Contractor.

(ii) Insurance of the works against fire etc. A. The Contractor shall in the joint names of the Owner and Contractor insure against loss or damage by fire, storm, tempest, lightning, flood, earthquake, aircraft or anything dropped there from, aerial objects, riot and civil commotion for the full value thereof all work executed and all unfixed materials good intended for, delivered to and placed or adjacent to the work., but excluding temporary building plant, tools and equipment owned or hired by the Contractor or any Sub-Contractor and shall keep such work materials and goods so insured until virtual Completion of the work. Such insurances shall be with insurers approved by the Architect and the Contractor shall be deposit with the Architect the policy or policies and the receipts in respect of premiums paid ; and should the Contractor make default in insuring or continuing to insure as aforesaid the Owner may himself insure against any risk with respect of which the default shall have occurred and deduct a sum equivalent to the amount paid by him in respect of premium from any monies due to or to become due to the Contractor. Providing always that if the Contractor shall independently of his obligations under this contract maintain a policy of insurance which covers ( inter alia ) the said work, materials and goods against the aforesaid contingencies to the full value thereof then the maintenance by the Contractor of such policy shall if the Owners interest is endorsed thereon, be a discharge of the Contractor’s obligation to deposit with the Architect a policy or policies and the receipts in respect of premiums paid. (This clause is applicable to the erection of a new building if the Contractor is required to insure against loss or damage by fire etc.) B. Upon settlement of any claim under the insurances aforesaid the Contractor with due diligences shall restore work damaged, replace or repair unfixed materials or goods which have been destroyed or repair unfixed materials or goods which have been destroyed or injured, remove or dispose of any debris and proceed with the carrying out and completion of the work. All monies received from such insurances shall be paid to the Contractor by instalments under certificates of the Architect issued at the period of interim certificate named in the appendix to these conditions. The Contractor shall not be entitled to payment in respect of the restoration of work damaged the replacement and repair of any unfixed materials or goods and the removal and disposal of debris other that the monies received under the said insurances. All work executed and all unfixed materials and goods intended for, delivered to and placed on or adjacent to the works ( expect temporary buildings, plant, tools and equipment owned or hired by the Contractor or any Sub-Contractor ) shall be a the sole risk of the Owner as regards loss or damage by fire, storm, tempest, lightning, flood, earthquake, aircraft or anything any loss or damage affecting the work or any part thereof or any such unfixed materials or goods is occasioned by any one or more of the said contingencies then (This Clause is applicable to the erection of a new building if the Owner is to bear the risk in respect of loss or damage by fire etc.) A. The occurrence of such loss or damage shall be disregarded in computing any amounts payable to the Contractor under or by virtue of this Contract. B. The Contractor with due diligence shall restore work damaged, replace or repair any unfixed materials or goods which have been destroyed or injured, remove and dispose of any debris and proceed with carrying out and completion of the work. The restoration of work damaged, the replacement and repair or unfixed materials and goods and the removal and disposal of debris shall be deemed to be variation required by Architect. The existing structure together with all the contents thereof and the works and all unfixed materials and goods intended for, delivered to and placed on or adjacent to the works ( except temporary buildings, plant, tools and equipment owned or hired by the Contractor or any Sub-Contractor ) shall be at the sole risk of the Owner as regards loss or damage by fire, storm, tempest, lightning, flood, earthquake, aircraft or anything dropped there from, aerial objects, riot and civil commotion, and the Owner shall maintain adequate insurance against that risk if any loss or damage affecting the work or any part thereof or any such unfixed materials or goods is occasioned by any one or more of the said contingencies then. (This clause is applicable to alterations of or extension to an existing building.)

LABOUR LAWS:

Contractor shall have valid PF, ESI registration. All laws related to Labour, PF, ESI, Medical insurance etc, shall be adhered to by contractor. No child Labour shall be employed by contractor.

GENERAL INSURANCE:

Contractor shall provide necessary insurance cover for all equipment and material in his scope till the system is handed over. Necessary insurance cover shall also be provided for man power employed on site. Contractor shall indemnify Owner/Engineer and their representatives employed and hold them harm less in case of any damages injuries /accidents and any claims arising out of them.

SUFFICIENCY OF SCHEDULE
The Contractor shall be deemed to have satisfied him before tendering as to correctness and sufficiency of his tender for works and prices quoted therein which shall cover all obligations under contract for satisfactory completion of works. In case of direct purchase of material by the Company, the Contractor will only receive the erection charges for such material as quoted.

SCHEDULE OF QUANTITIES AND DRAWINGS

The schedule of quantities indicates nearest approximate quantities of the items of works. There is possibility of upward or downward variation of quantities due to Site modifications variation of quantities up plus / minus 10% of the quantities as per schedule shall be accepted by Contractor without any financial implication. The Contractor shall take exact measurements for items like cables, earth strips prior to bringing and cutting the same. If variation is beyond above stipulated limits such items shall be carried out after written mutual agreement

The drawings enclosed indicate extent and general arrangement of various equipment. These are for guidance of Contractor and exact dimensions, locations, clearance governed by Site conditions, buildings and statutory rules. The Contractor is required to go through the drawings and regulations prior to starting of works. Any discrepancy / changes required shall be reported to ARCHITECT / ELECTRICAL CONSULTANT and the Company. The Contractor shall prepare all working drawings and get them approved from the ARCHITECT / ELECTRICAL CONSULTANT prior to starting the Work

AUTHORITY AND LAW 
The Contractor shall confirm to all provisions of any Law that are and/or may be applicable to Works of any Governmental Authority or any Person

SUPERVISION
A competent Authorized Representative of the Contractor shall be available at Site, for supervision of works, co-ordinating, receiving instructions from ARCHITECT / ELECTRICAL CONSULTANT /Company, during entire period of contract

ACCESS TO WORK
The ARCHITECT / ELECTRICAL CONSULTANT /Company /PMC or their respective Authorized Representative shall have access, to Works being carried out at all reasonable times. No person not authorized by ARCHITECT / ELECTRICAL CONSULTANT /Company /PMC except representatives of Government Authorities shall be allowed at the Site at any time

SUB-CONTRACT: 
The complete Work included in the contract, shall be executed by the Contractor, and the Contractor shall not sub-contract / sub-let work or part thereof, without prior express written consent from the ARCHITECT / ELECTRICAL CONSULTANT /Company /PMC. However, the Contractor shall not be relieved from the responsibility, of execution of works, as per contract under any circumstances

DATE OF COMMENCEMENT
The Contractor shall take up commencement of work immediately, after the execution of the Agreement with the Company

CO-ORDINATION
The Contractor or his Authorized Representative shall be responsible for co-ordination with all other agencies working at the Site for smooth functioning and timely completion of the Work. 
Site meetings as necessary weekly or bi-weekly shall be attend by qualified / responsible Authorised Representative from the Contractor’s side to take Site instruction / decision in view of troubleshooting and progress review of Works. The ARCHITECT / ELECTRICAL CONSULTANT / PMC his Authorized Representative shall attend the meeting. As a special requirement of this project the Contractor shall send visual proofs of work progress in form of photographs to the Company and the ARCHITECT / ELECTRICAL CONSULTANT periodically

MEASUREMENTS
The measurements of completed work shall be taken jointly from time to time as mutually agreed. The Contractor shall send his Authorized Representative for assisting the Company and/or the ARCHITECT or their respective Authorized Representatives for measurements and shall furnish all particulars required to complete the measurements.

COMPLETION CERTIFICATE
The Work shall be deemed to have been completed on production of a written certificate by the Authorised Representative of the ARCHITECT / ELECTRICAL CONSULTANT that they have been finally completed. The “Defect Liability Period” shall commence from the date of such final completion certificate

DRAWINGS
ARCHITECT / ELECTRICAL CONSULTANT will prepare working drawings and issue them to tender wining contractor. These working drawings will comprise of various layouts and single line diagram (SLD). These drawings will be according to inputs, instructions received from all service consultants and architect. Contractor is expected to start the work only after getting approval from ARCHITECT / ELECTRICAL CONSULTANT for the shop drawings prepared by him.
During progress of work there may be some alteration, addition, deletions introduced by Client or Consultant or Architect, such alterations shall be incorporated in Shop Drawings in further revisions and he shall take approval from respective authority before execution.
Working Drawings do not cover the drawings, which are to submit to various authorising agencies (Power Supply Company, Electrical Inspector, Local Authority etc.). Such drawings are required to be in particular prescribed format by respective authorities hence contractor will prepare their drawings based on working drawings and approved shop drawings.
The list of working drawings and shop drawings will be issued to ARCHITECT / ELECTRICAL CONSULTANT at the time of commencement of project.
Contractor shall take care to prepare all the drawings in CAD format (Soft), with a proper care to make them in readable when printed.

Following technical details should be submitted by contractor to Client/Electrical consultant/Architect before procurement of any material.

- Data sheet

- Make of Material

- Performance Specification

- Technical catalogue & literature

- Installation Manual/Details

- Guarantee formats

- Test Certificates

- Service facility available

COMPLETION DRAWINGS-(AS BUILT DRAWINGS): 
On completion of Works prior to getting completion certificate, the Contractor shall prepare as built drawings in association and to satisfaction of the ARCHITECT / ELECTRICAL CONSULTANT giving all particulars

Exact dimensions and clearances

Fuse and switchgear ratings, ratings of equipment’s

Cable sizes

Cable tags details

Earthing details 
The Contractor shall also provide detailed drawings, instruction and maintenance manuals and test, repairs for all bought out items

TECHNICAL SCRUTINY OF FINAL BILL
The Company shall have the right to get works and bills technically scrutinised at the time of payment of final bill from the ARCHITECT. The Company shall be entitled to recover any money found to be over paid or over certified during the period of execution of the contract Work

REMOVAL OF WORK
The Company and/or the ARCHITECT / ELECTRICAL CONSULTANT during the progress of the Work have powers to order in writing the removal from the Site any material / installation which in their opinion are not as per specifications or instructions for carrying out Works within specified time and the Contractor shall carry out such removals / reworks as per specification at his own cost

DEFECT LIABILITY PERIOD: 
Any defect, fault, deterioration in performance of the material, workmanship and installations which may appear; during the “Defect Liability Period” of twelve months from date of the final completion certificate issued by the ARCHITECT / ELECTRICAL CONSULTANT shall be amended / made good by the Contractor at his own cost within a reasonable time. In case of default the Company may employ and pay other Person to make good the defects and deduct the expenses from the dues payable to Contractor on certification from ARCHITECT / ELECTRICAL CONSULTANT

RESPONSIBILITY: 
The Contractor shall be responsible for injury to Person, animal or things for all damages caused to property from operations of neglect by himself or his employees, Authorized Representatives and/or sub-contractors
The damages to the property, plant and equipment caused due to such negligence or wilful act or omission of the Contractor or its employees, representatives and/or sub-contractors shall be made good by the Contractor at his own cost to satisfaction of the Company within a specific time. The  Contractor shall indemnify the Company against all claims which may be made against the Company by any member of the public or other third party in respect of anything, which may arise in respect of the Works or in consequence thereof and shall at his own expense arrange to effect and maintain, until the final completion of the contract, with an approved policy of insurance in the joint names of the Company and the Contractor against such risks and deposit such polices with the ARCHITECT / ELECTRICAL CONSULTANT from time to time during the occurrence of this Agreement. The  Contractor shall similarly indemnify the Company against all claims, which may be made upon the Company whether under the applicable labour laws or any other statute in force during the currency of the Agreement and till the expiry of the Defective Liability Period, or at common law in respect of any employee of the Contractor or any sub-contractor and shall at his own expenses effect and maintain until the policy of insurance in the joint names of the Company and the Contractor against such risks and deposit such policy or policies with the ARCHITECT / ELECTRICAL CONSULTANT from time to time during the currency of the Agreement
The Contractor shall be responsible for anything, which may be excluded from the insurance policies above referred to and also for all other damages to any property arising out of and incidental to the negligence or defective carrying out of his contract. He shall also indemnify the Company in respect of any costs, charges or expense arising out of any claim or proceeding and also in respect of any award of or compensation of damage arising therefore
The Company in consultation with the ARCHITECT / ELECTRICAL CONSULTANT shall be entitled to deduct amount of damage, compensation loss arising from such damages / injuries / accidents in case of default 
In addition to the above, the Contractor shall indemnify the Company from and against any and all losses, damages, charges, claims and expenses, including reasonable attorney’s fees arising from claims or arising from or in relation to the following

Any workmanship in relation to the erection or installation which is later on found to be inaccurate or incomplete or faulty

Any breach or violation of any of the terms and conditions of or any obligation arising under the proposed Agreement; and

Any representation or warranty found to be false or misleading in any manner whatsoever

LIQUIDATED DAMAGES
The Contractor shall pay liquidated damages of 0.5 % per day subject to a maximum of 5 % of value of tender document in case of delays attributed to him against agreed time plan on each milestones.

TERMINATION OF CONTRACT
The Company shall be entitled to terminate the Agreement , in case the Contractor fails to fulfil one or more conditions of contract, or if ARCHITECT / ELECTRICAL CONSULTANT certifies to the Company in writing that the Contractor has abandoned the contract has failed to commence the Work or has without any lawful excuse under contract conditions suspended the Work for more than one week has failed to proceed with the Work and failed to make such due progress for timely completion of the Work has failed persistently to observe and perform the Work as per specifications and contract conditions; and has employed services of sub-contractors / sub-let all or part of the Works without prior permission of the Company/the ARCHITECT / ELECTRICAL CONSULTANT In any of above said cases the Company, can terminate the Agreement after giving seven days’ notice in writing to the Contractor In cases of dispute, the contractor shall be at liberty to terminate the contract by giving thirty (30) days prior written notice to the Company. The Company shall also be entitled to recover any losses due to default of Contractor, incurred by him for carrying out / completing Works as certified by the ARCHITECT / ELECTRICAL CONSULTANT

CERTIFICATION AND PAYMENT 
The Contractor shall be paid by the Company from time to time under interim measurements certified by ARCHITECT / ELECTRICAL CONSULTANT on account of work executed in accordance with the contract and to the satisfaction of ARCHITECT / ELECTRICAL CONSULTANT with retention till the work is completely executed. On virtual completion of the works contractor shall be paid final instalment retaining five percent (5%) over a period known as “Defect Liability Period” as security. The final balance shall be payable to the contractor after expire of “Defect Liability Period” and after such certificate is issued by engineer / consultant.
Engineer / consultant shall have power to withhold payment against work or part thereof is not carried out to his satisfaction

ARBITRATION 
All the disputes of any kind in connection with contract shall be referred to the ARCHITECT / ELECTRICAL CONSULTANT and settled in writing with him. If any party is dissatisfied with such decision, except for clauses indicated in clause 21 they are entitled to bring such disputes for arbitration
Arbitrator / s shall be appointed by both parties in accordance with the provisions of the Arbitration and Conciliation Act, 1996 and his / their decision shall be final and binding on both parties

PRICES: 
The prices quoted in the schedule of works shall remain firm during the period of contract. Bidder shall clearly state taxes, statutory duties and levies which vendor is required to pay. Sales tax/VAT shall be to the Contractor’s account and that the Contractors will indemnify the Company for any liability incurred by the Company in this behalf.  Escalation of rates is not applicable for any reason. There are some items for “RATE ONLY” OR WITH QUANTITY AS ZERO (0). If the rates for such items are not quoted then the rate will be considered as zero (0), and will be used for bill certification.
As a special condition for this project, the electrical power and water required for execution work will have to be arranged by the contractor at his own cost. Client will not make any type of arrangement or provide any type of help in arranging these. Contractor shall take care of these expenses while preparing quotes.

EXTRA ITEMS AS REQUIRED BY COMPANY: 
The Contractor shall be required to carry out extra items due to Site requirements or changes. The Contractor shall carry out all such items after written consent from the Company. The Contractor shall submit a rate analysis of these items based on market rates. A margin of 10% shall be allowed over and above the expenses incurred. Escalation shall not be allowed on the extra items.

The cost of such extra Item should not exceed than 5% of the contract value.

PERFORMANCE GUARANTEE
The contractor shall guarantee performance of plant and equipment and workmanship against fault for a period of 12 months called as “Defect Liability Period” from the date of the final completion certificate
5% of work value shall be retained for the entire “Defect Liability Period” as security. Such retention can be released on furnishing a bank guarantee of a nationalized bank that is acceptable to the Company for the retention amount in favour of the Company

TERMS

Bills to be raised on monthly basis. Minimum bill value shall be 10% of contract value

Approval of the Bill:

Contractor will submit the bill of completed activity every month to ARCHITECT / ELECTRICAL CONSULTANT Office. Certification of bill will be made by CONSULTANT, within 30 days of receipt of bill to ARCHITECT’S office.

Payment will be released after 15 days from the receipt of bill with payment certificate from ARCHITECT.

Defect Liability Period: 365 days from the date of final completion.

Final completion: The date on which the final certificate is issued & received from consultant to the client’s office.

Period of Final Bill Certification: 60 days from the date of the final bill received at the ARCHITECT’S office.

Some where we need to metion about working timing (No work in night)

PAYMENT TERMS:

| Stage of payment | Percentage of Material cost as per order | Percentage of Installation cost as per order. |
| --- | --- | --- |
| Advance | 0 % | 0% |
| Advance Against Delivery of material on site. | 60% | 0% |
| Against completion | 20% | 80% |
| Against Testing | 10% | 10% |
| Against total Commissioning | 05% | 05% |
| After Defect liability period | 5% | 5% |
| Total payment | 100% | 100% |

## PACKING AND FORWARDING

SCOPE
This specification covers equipment /material packing transportation and protection of material during transit and storage. 
PACKING: 
Vendor shall be responsible for any damage during transit due to improper or insufficient packing 
Packing shall be constructed out of sound material and dimensions suitable to the goods, size and weight Fragile material shall be security braced within container or amply fastened to prevent shifting or battering. Cushion lining of appropriate material shall be provided wherever necessary 
Loose material MS parts Nuts bolts etc, shall be packed separately in gunny bags with polythene bags sealed and tagged Components containing glass shall be provided with shock absorbing material cover like thermo Cole. In case of bulk materials Vendor shall supply the same in minimum sub assemblies within the transport limitation Care shall be taken for preventing any seepage of water in case required to prevent any corrosion during transport 
All spare parts shall be separately packed and treated for long storage in site condition 
Each crate/package shall contain a packing list in waterproof envelope 
Vendor/Contractor shall supply any material found short inside the packing at no extra cost 
All packing material shall become property of Contractor as the purchaser 
All packages shall be clearly, legibly and durably marked on the least two sides 
Destination address 
Dimension and weight 
Sign showing “ Side up “ with arrow 
Sign “Fragile and Handle with care” for delicate equipment 
Slinging and sling positions 
Important handling and unpacking instructions

Transport: 
No material shall be dispatched without prior consent shipping clearance by the ARCHITECT/purchaser The vendor shall intimate in advance date of dispatch and probable date of delivery at Site so that unloading arrangements can be made, particularly for heavy material
N case any equipment is to be transported in sub-assemblies or parts, vendor shall furnish all particulars and match marking. Such sub-assemblies shall be well within transportation and handling limitations the transporters shall be provided with proper address and other details, working hours etc 
the crate or packages shall be properly secured to avoid movements during transit to minimise possibility of damage

Specific equipment

Transformer shall be shipped with oil. Radiators shall be supplied separately in case of transport limitations Switchgear cubical shall be packed and dispatched in separate and convenient sections. All withdraw able equipment like circuit breakers; arc chutes shall be packed and shipped separately. All the relays and instruments shall be packed and shipped separately with operating mechanism temporarily arrested Batteries shall be dispatched to Site in dry uncharged condition. Appropriate quantity of electrolyte of correct specific gravity shall be packed in not returnable porcelain jars in steel wire baskets

Cables shall be dispatched in no returnable wooden drums with adequately sealed cable ends

SAFETY REGULATIONS

All the work to be executed based on the Permit To Work (PTW) format issued by Client

Readily accessible First aid kit including adequate sterilised cotton and dressing shall be provided

Any injured person shall be taken to nearest hospital

All workmen working at heights shall be provided with safety belts and anchoring arrangements at the site

Portable ladders shall be of heights less than 8 feet. In case of ladders additional manpower shall be employed for holding the ladders

Workers engaged in welding and related work shall be provided with protective eye shields and gloves.

The excavation, trenches shall be provided with necessary lighting and obstacles

All electrical connections taken for construction purpose shall have earthing provided for equipment earthing

Open/temporary jointing of the cables shall be avoided

Live wires shall not be laid on ground/road or taken on surface without protective cover

All water pumps underground or otherwise shall have covers

APPENDIX HEREINBEFORE REFERRED IN

| SR. NO. | CLAUSE | GENERAL CONDITIONS OF CONTRACT |
| --- | --- | --- |
| 1 | GUARANTEE PERIOD / DEFECT LIABILITY PERIOD | A PERIOD OF 12 MONTHS FROM THE DATE OF COMMISSIONING |
| 2 | DATE OF COMMENCEMENT | FROM DATE OF LOI |
| 3 | AGREED LIQUIDATED DAMAGES | PENALTY @ 0.5% PER DAY SUBJECT TO MAXIMUM OF 5% OF THE ORDER VALUE FOR THE DELAY IN THE DELIVERY OF MATERIAL & COMPLETION OF INSTALLATION BEYOND COMPLETION DATE. |
| 4 | RETENTION | 5 % OF TOTAL CONTRACT VALUE |
| 5 | PAYMENT TERMS | AS MENTION IN PAYMENT TERMS CLAUSE |
| 6 | ELECTRICAL POWER AND WATER REQUIRED FOR EXECUTION WORK | TO BE ARRANGED BY THE CONTRACTOR AT HIS OWN COST. |

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)

DEVIATIONS FROM GENERAL CONDITIONS OF CONTRACT

All deviations from general condition of contract shall be filled in hereby the bidder.

SECTION			CLAUSE NO.			DEVIATION

The bidder hereby certificates that the above mentioned are only deviations from general Conditions of contract of enquiry.

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)

DEVIATIONS FROM TECHNICAL SPECIFICATIONS

All deviations from technical specifications of contract shall be filled in hereby the bidder.

SECTION			CLAUSE NO.			DEVIATION

The bidder hereby certificates that the above mentioned are only deviations from technical Specifications of this enquiry.

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)

FORMAT OF THE AGREEMENT WITH CONTRACTOR

Agreement Made on the 		
between

Represented by

AND

Having (or whose registered office is situated at)

Represented by

(Hereinafter called “The Contractors”) OF THE OTHER PART.

Whereas the Client is desirous of electrification of

(Hereinafter called “Work”) and has caused Drawing and bills of Quantities showing and describing the work to be done to be prepared by or under direction of Client/ consultant.

And whereas the contractor has supplied the Client with a fully priced copy of the said Bills of Quantities (Which copy hereinafter referred to as “the Contract Bills”)

And whereas the said Drawings (hereinafter referred to as “the Contract Drawings”) and the contract bills have been signed by or on behalf of the parties hereto:

NOW IT IS HEREBY AGREED AS FOLLOWS:

- For the consideration hereinafter mentioned the contractor will upon the subject to the conditions annexed carry out and complete the work shown upon the contract drawings and described by or referred to in the contract bills and in the said conditions.

- The Client will pay the contractor the sum of Rs. 			 Only 
(Rupees only) (hereinafter referred to as “the Contract Sum”) or such other sum as shall become payable hereunder at the times and in the manner specified in the said conditions.

- The said conditions and appendix thereto shall be and construed as forming part of this agreement and the parties hereto shall respectively abide by, submit themselves to the conditions and perform the agreements on their parts respectively in such conditions contained.

For

As witness our hands this XX day of 2022

Signed by the said

In the presence of

Witness

Signed by the said

In the presence of

Witness

Project details

- HT AND LT SUPPLY RELATED ELECTRIFICATION  WORK ( FROM ADJOINING MSEB DISTRIBUTION TRANSFROMER TO LT PANEL SUBSTATION AND LT PANELS IN THE NEW BUILDING PREMISES)

- DG SET CABLES LAYING AND INTERCONNECTION OF THE DG SETS WITH LT PANELS.

- 1 NO. OF 1000 KVA TRANSFORMER SET ERECTION WORK.

- ELECTRIFICATION WORK RELATED TO SUPPLY AND ERECTION OF  DBS , CABLE TRAYS, CABLES AND END TERMINATIONS, POINT WIRING AND MAINS WIRING,  SUPPORTING STRUCTURES AND RELATED FABRICATION WORK,  EARTHING STATIONS ETC.

- DATA NETWORKING AND OTHER RELATED ELV WORK

Scope of Works

Electrical contractor scope is to design, supply, testing (FAT & SAT), loading, transfer to site, unloading, shifting to store, installation, calibration of meter & equipment at site, commissioning & training on operation and maintenance of following material to client to meet the successful operation and functional requirements as per Electrical norms, practices and local standards which suits all the statutory requirement to put into the operation.

- 1000 kVA TRASNFORMER and related erection work.

- HT SWITCHGEAR and related erection work

- HT & LT cables

- HT & LT Cable glands

- LT panels and DBs

- Cable trays

- Supports for light fixtures and trays.

- Mains and Point wiring work

- Modular switches & socket outlets

- PVC Heavy duty conduits & its accessories, wires, etc

- Earthing station, Earth strips and earthing materials.

- Lighting protection system.

- Access control work

- Miscellaneous works required for system completion

- Liaison & obtaining all necessary approvals from statutory authorities

- Preparation of drawings in necessary format, follow up & arranging approval of drawings, scheme by all local authority additional connected load sanction from MSEDCL.

- Preparation of Shop Drawings based on tender drawing before execution of work.

- Testing of all systems.

- Preparation of As Built Drawings after completion of all work.

- All necessary civil work like making penetrations, making earth chambers, grouting of frames supports etc.

- All consumable hardware

- Any other items specified in Schedule of Quantities

Scope also includes transporting, unloading, receiving, inspection, storing, transportation to work site, handling, assembling, removing of scrap material from working area, cleaning, mechanical erection, chipping of foundations, installation, alignment, testing and commissioning & handing over in working condition of all items covered above but not limited to it.

Minor civil works like drilling and punching holes and openings in concrete floors, slabs, chasing of brick walls/ceiling and after chasing brick walls/ceiling filling the jerry work, fabrication of supporting structures, drainage of water from cable trenches, cleaning and clearing of all debris due to electrical installation.

The extent of work services under the contract include all items shown on the drawings, indicated in companion with specifications, notwithstanding the fact that such items have been omitted from the price schedule. All equipment’s and services which are required to complete the intent of the contract shall also be deemed to be within the scope of the contract.

After receiving/inspections of not only the materials supplied by contractor but also those supplied by the Client, shall be reported to the Client/Consultant with their comments.

Preparation of execution drawings based on the drawing submitted with tender document. Preparation of master SLD, SLD for DBs (PDB & LDB), conduit layout for lighting & power and as built-in- drawings in vendor scope only. Tender document contains the main cable tray, lighting, power point layout & Major SLDs. Electrical contractor must develop detailed drawing further up to the equipment termination with sizing, support structure (From wall or ceiling) with sections in between each grid & submit the same for approval.

Co-ordination with other service contractors with respect to the installation activity without affecting the project schedule is in this scope of contract.

Furnishing of all labour, skilled and unskilled, supervisory and administrative personnel, erection tools and tackles, testing equipment, implements, supplies, consumables like welding rods and gas, oil and grease, cleaning fluids, insulating tape, anti-corrosive paints, jute cotton waste etc. and hardware for timely and efficient execution of the erection work.

Transport vehicles necessary for efficient transportation of equipment from employer’s stores to site of erection and excess materials back to employer’s stores.

Complete assembly, erection and connection, testing and commissioning, putting into successful and satisfactory operations of above equipment as per local requirement & general practices.

The items of work to be performed on all equipment and materials shall include but not be limited to the following:

- Receiving, unloading and transportation at site. (To client / contractor’s stores and from there up to actual place of erection).

- Opening, inspecting and reporting all damages & short supply items.

- Arranging to repair and/or re-order all damaged and short supply items.

- Inspection of all equipment, which are not inspected at manufacturer’s works by employer regarding compliance with technical specifications and submission of report of the same to site in charge.

- Storing at site with suitable all-weather protection.

- Assemblies, erection and complete Installation.

- Necessary coordination between works done by other contractors.

- Final check-up, testing and commissioning in presence of client/consultant’s representative.

- Trial run for thirty (30) days, rectification of defects, if any and adjustments as necessary.

- Obtaining employer’s written acceptance of satisfactory performance.

- Liaison & obtaining all necessary approvals from statutory authorities.

The Vendor shall submit the technical requirements, data and technical data sheets for the items purchase by him. The Vendor shall furnish catalogues, engineering data, technical information, design documents, drawings etc., fully in conformity with the technical specification.

Unless brought out clearly, the Vendor shall be deemed to confirm to this specification scrupulously. All deviations from the specification shall be clearly brought out in the respective schedule of deviations. Any discrepancy between the specification and the catalogues or the bid, if not clearly brought out in the specific requisite schedule, will not be considered as valid deviation.

Equipment’s furnished shall be complete in every respect with all mountings, fittings, fixtures and standard accessories normally provided with such equipment and / or needed for erection, completion and safe operation of the equipment as required by applicable codes though they may not have been specifically detailed in the Technical Specification unless included in the list of exclusions.

Materials and components not specifically stated in the specification but which are necessary for commissioning and satisfactory operation of the electrical work unless specifically excluded shall be deemed to be included in the scope of the specification and shall be supplied without any extra cost. All similar standard components/parts of similar standard equipment provided, shall be inter-changeable with one another.

Sundry material:

The sundry material to be supplied shall be of high quality, brand new and of reputed make. The make and sample of each material shall be approved in writing by client/PM/consultant. Only those approved samples shall be kept with PM/ Consultant till the completion of job. If the supplied material does not conform to the sample, the material will be rejected at any time without assigning any reasons.

- Sundry Materials are:

- Industrial type cable glands

- Cable Lugs

- Cable tag for identification

- Cable route Marker

- Insulation Tape

- Interlocked cable tile

- Bolts, washer & Nuts Etc…

Transportation:

Equipment and materials to be supplied by contractor shall be mainly available in the Construction Stores, which is within the site premises. These shall generally be in packed condition. Contractor shall transport the equipment, (lift it, if necessary) till it reaches the exact location where it is to be installed, strictly as per manufacturer / consultant’s instructions. Contractor shall un-pack the equipment at its plant location, or elsewhere as required as per PM requirement. Any defect found while unpacking the equipment

Shall be immediately informed to PM Engineer in writing.

Standards and specifications

All Works are required to be designed and executed in accordance with the appropriate local codes, regulations, specifications And requirements specified in the Contract and the tender offer is deemed to include this requirement.

Codes and standards:

The supply and installation of equipment shall be in accordance with the established codes, sound engineering practices and must conform to the statutory regulations. The main codes and standards, which shall be considered minimum required are as follows. Latest version of these shall be followed:

LIST OF APPLICABLE INDIAN STANDARDS FOR ELECTRIFICATION WORK

| Sr. No | STANDARDS | TITLE |
| --- | --- | --- |
| 1 | IS:732 - 1989 | Code of practice for electrical wiring installations. |
| 2 | IS:4648 - 1968 | Guide for electrical layout in residential buildings. |
| 3 | IS:8061 - 1976 | Code of practice for design, installation and maintenance of service lines up to and including 650V. |
| 4 | IS:8884 - 1978 | Code of practice for installation of electric bells and call system. |
| 5 | IS:5578 - 1985 | Guide for marking of insulated conductor. |
| 6 | IS:11353- 1985 | Guide for uniform system of marking and identifications of Conductors and apparatus terminals. |
| 7 | IS:5728 - 1970 | Guide for short-circuit calculations. |
| 8 | IS:7752(Part-1)-1975 | Guide for improvement of power factor in consumer installation: Low and medium supply voltages. |
| 9 | IS:3646(Part-1)-1966 | Code of practice for interior illumination: Principles for good lighting and aspects of design. |
| 10 | IS:3646(Part-2)-1966 | Code of practice for interior illumination: Schedule of illumination and glare index. |
| 11 | IS:2672 - 1966 | Code of practice for library lighting. |
| 12 | IS:10118(Part-1)-1982 | Code of practice for selection, installation and maintenance of switchgear and control gear: General. |
| 13 | IS:10118(Part-2)-1982 | Code of practice for selection, installation and maintenance of switchgear and control gear. |
| 14 | IS:10118(Part-3)-1982 | Code of practice for selection, installation and maintenance of switchgear and control gear: Installation. |
| 15 | IS:10118(Part-4)-1982 | Code of practice for selection, installation and maintenance of switchgear and control gear: Maintenance. |
| 16 | IS:2309 - 1989 | Code of practice for the protection and allied structures against lightning. |
| 17 | IS:3043 - 1987 | Code of practice for earthing |
| 18 | IS:5216(Part-1)-1982 | Guide for safety procedures and practices in electrical work: General |
| 19 | IS:4237 - 1983 | General requirements for switchgear and control gear for voltages not exceeding 1000 V AC or 1200 V DC. |
| 20 | IS:6875(Part-1)-1973 | Control switches (switching devices for control and auxiliary circuits including contractor relays) for voltages upto and including 1000 V AC and 1200 DC: General requirements and tests. |
| 21 | IS:4064(Part-1)-1978 | Air break switches, air break dis-connectors, air-break Switch dis-connectors and fuse-combination units for voltages not exceeding 1000 V AC or 1200 DC: General requirements. |
| 22 | IS:8828 - 1978 | Miniature air break circuit breakers for voltages not exceeding 1000 volt. |
| 23 | IS:13032 - 1991 | Miniature circuit breaker boards for voltages up to and including 1000 volts AC. |
| 24 | IS:12640 - 1988 | Residual current operated circuit breakers. |
| 25 | IS:2959 - 1985 | Contactors for voltages not exceeding 1000 V AC or 1200 V DC. |
| 26 | IS:8623(Part-1)-1977 | Factory built assemblies of switchgear and control gear for voltages upto and including 1000 V AC and 1200 V DC: General requirements. |
| 27 | IS:8623(Part-2)-1980 | Factory assemblies of switchgear and control gear for voltages upto and including 1000 V AC and 1200 V DC :Particular requirements for busbar trunking system (busways). |
| 28 | IS:694 - 1990 | PVC Insulated cables for working voltages upto and including 1100 V. |
| 29 | IS:1554(Part-1)-1988 | PVC insulated (heavy duty) electric cables : For working voltages upto and including 1100 V. |
| 30 | IS:3961 (Part-5)-1968 | Recommended current ratings for cables: PVC insulated light duty cables. |
| 31 | IS:9537(Part-1)-1980 | Conduits for electrical installations: General requirements. |
| 32 | IS:9537(Part-2)-1981 | Conduits for electrical installations Rigid steel conduits |
| 33 | IS:3480 - 1966 | Flexible steel conduits for electrical wiring. |
| 34 | IS:2667 - 1988 | Fittings for rigid steel conduits for electrical wiring. |
| 35 | IS:3837 - 1976 | Accessories for rigid steel conduits for electrical wiring. |
| 36 | IS:5133(Part-1)-1969 | Boxes for enclosure of electrical accessories: Steel and Cast-iron boxes. |
| 37 | IS:371 - 1979 | Ceiling roses. |
| 38 | IS:3854 - 1988 | Switches for domestic and similar purposes. |
| 39 | IS:4615 - 1968 | Switch socket outlets (non-interlocking type). |
| 40 | IS: 4160 - 1967 | Interlocking switch socket outlet. |
| 41 | IS:1293 - 1988 | Plugs and socket outlets of rated voltage upto and including 250 volts and rated current up to and including 16 amperes. |
| 42 | IS 15652:2006 | Electrical Insulation mat. |
| 43 | NBC 2016 | National Building Code Part-3, 4 & 8 |
| 44 | Electricity code | Indian Electricity Supply Rules &Act , latest edition |
| 45 | NEC | National Electric code |
| 46 | ASHRAE | ASHRAE Standard 90.1 2004 |

Following codes must be adhered to for Electrical Works:

Indian standard Specifications

Indian Electricity rules and regulations

National building code

IEEE Standard

IEC 61439-1-2 - Low-voltage switchgear and control gear assemblies

IEC 62305 - For Lightning Protection

IEEE Standard 1100- 1999: Recommended Practice for Powering and Grounding Electronic Equipment

General Scope of Electrical Work

This specification details the broad guidelines for unload, store, erect, testing and commissioning of all the equipments required for the Electrical Works Tender Installation. The contractor shall furnish all the labour, tools and equipments for the electrical works, as shown in the accompanying drawings and in the bill of quantities and specifications hereinafter described and execute the works as directed by the Client/Consultant and completed to their entire satisfaction.

Contractor

The Contractor shall be a licensed Class One or 'A' class Electrical Contractor, possessing a valid Electrical Contractor's license in the State, employing licensed supervisors and skilled workers having valid permits as per the Regulation of Indian Electricity Rules and Local Electrical Inspectors requirements. He should have executed electrical works of this magnitude earlier and shall have qualified engineers to produce execution drawings and to supervise the work at site.

Minimum Requirement of Technical Staff:- ( AT SITE)

One qualified, and competent experienced Engineer - Minimum 10 years’ experience in executing similar installations acceptable to the Clients/Consultant.

Diploma Holders with at least 15 years site experience also acceptable to the Clients/Consultant.

Contractor must depute one certified safety officer at site for full time basis.

Experienced and certified cable jointers. - Minimum of 1 No.

Experienced Wireman. - Detail manpower-loading chart to be furnished.

Contractor must submit site organogram of the project execution team.

Minimum Equipment Required at Site: -

| Multi-meter, 1000/5000 V Megger, Earth Megger & Lux Meter | 1 No. Each Duly calibrated and certified by third party agency. |
| --- | --- |
| Tool kit containing, Double end spanners, Ring spanners | 1 Set for each Technician. |
| Spanners, Screw Drivers, Hammers, chisels etc. 5 Mtrs. Steel tapes | 1 No. for each skilled Technician |
| 30/100 M steel tape for recording measurements | 1 No. |
| Spirit level 450 mm long metal body | 1 No. (Per Team) |
| Hand Grinder | 1 No. (Per Team) |
| Hand drilling machine 1" HSS/Masonry | 1 No. (Per Team) |
| Pedestal drilling machine 5/8" | 1 No. |
| Vices fixed to Tables | As required. |
| H.S.S / Masonry (mm) drill bits up to 25 mm | As required. |
| Hydraulic cable crimping device | Size / Quantity (As required) |
| Any other testing equipment as required | 1 Set. Each. |
| Continuity checker/tester | 1 no. for each skilled Technician |
| First Aid approved kits | 1 Set per Building & additional Quantities as required. |

Site Engineer

The Contractor shall employ a competent, licensed qualified full time electrical Engineer to direct the work of electrical installations in accordance with the drawings and specifications. The Engineer shall be available at all times on the site to receive instructions from the Consultant/Client in the day to day activities throughout the duration of the contract. The Engineer shall correlate the progress of the work in conjunction with all the relevant requirements of the supply authority. The skilled workers employed for the work should have requisite qualifications and should possess competency certificate from the Electrical Inspectorate of Local Administration.

Application for Power Supply, Fees, Permits, Tests and Inspection/ Approval by Local Authorities

The contractor shall be responsible for filling and follow up of application for getting the drawings/scheme approved by the Electrical Inspector and finally the whole installation shall be got approved by the Electrical Inspector. The contractor shall pay all fees and the same shall be reimbursed by the Clients at actual on submission of receipts. On completion of this work, the contractor shall obtain and deliver the certificate of final inspection and approval by the Local Electrical supply authority to the Consultant/Clients. The Consultant/Client shall have full powers to require the materials or works to be tested by an independent agency at the Electrical Contractors expenses in order to establish their soundness and adequacy.

Drawings

The drawings and bill of quantities shall be considered as a part of this contract and any work shown on the drawings and not called for in the drawing or vice-versa, shall be executed as if specifically called for it. The Execution drawings indicated the extent and general arrangement of various equipment, conduits and its wiring, etc. and are essentially diagrammatic. The drawings broadly suggest the routes to be followed. The work shall be installed as indicated on the drawings. However, any minor change if found essential to co-ordinate the installation of this work with other trades shall be made without any additional cost to the Clients. The drawings are for the assistance and guidance of the contractor only and the exact location, distances and levels, etc. will be governed by the space conditions.

The contractor shall examine all Architectural, Structural, Plumbing, Utility, Air Conditioning and Electrical drawings before starting the work and prepare its own execution drawings containing all details. Any discrepancies which in his opinion appear on them have to be reported to the Consultant/Clients and get them clarified. They shall not be entitled to any extras, for omissions or defects in electrical drawings or when they conflict with other work.

Drawings Submissions

Consultant shall provide the Main Cable tray, Lighting, Power Point, Earthing Layout and other drawings with the tender. Electrical contractor has to develop shop floor drawing further up to the equipment termination with sizing, all support & section drawings and submit the same for approval. The final approved copy of the drawing has to release for execution. Contractor will dully sign & approve all the drawings before execution of work.

The contractor will prepare conduits layout drawing wherever Point wiring is applicable and shall submit for Approval.

Above all drawing shall submit within 20 days of signing the contract.

As built drawings/operation and maintenance manual inspection and test report:

The contractor shall submit minimum 5 sets of original drawings with native, editable & PDF copy of all as built drawing. Operation and maintenance manual with properly documented shall be submitted in 3 sets for all equipments supplied and erected by the contractor.

NOTE: Failing to comply with the above, will result in withholding the release of the retention money and any other payments to the contractor and issue of virtual completion certificate.

General

The Contractor shall furnish all tools, welding equipment, testing equipment, test connections and kits, etc. required for complete installation, testing and commissioning of the items included in the contract work.

The contractor shall co-operate through the Consultant/Client/Engineer with other contractors at site, in all matters of common interest, so as not to obstruct operation of others and to ensure the safety of all personnel and works covered under this specification.

The work shall be carried out strictly as per the instructions and execution drawings. In case of any doubt/misunderstanding as to correct interpretation of the drawings or instructions, necessary clarifications shall be obtained from the Client/Consultant. This contractor shall be held responsible for any damage to the equipment consequent to not following the Manufacturer's instructions correctly. All necessary drawings, Manufacturer's equipment manuals shall be furnished to the Clients and a copy to consultant.

Contractor will be the responsibility for their material at site after receiving from the supplier, till the installation, commissioning and handed over to client. If any theft happens after installation & before handing over, then it is contractor responsibility to arrange the material as per the requirement & complete the job at free of cost.

The Contractor shall have a separate cleaning team to clean all equipment under erection and as well as the work area at regular intervals to the satisfaction of the Client/Consultant. In case the cleaning is not up to the Client's satisfaction, they will have the rights to carry out the cleaning operations and any expenditure incurred by the Client in this regard will be to the Contractor's account.

In order to avoid hazards to personnel moving around the equipment such as switchgear, etc. which is kept charged after installation before commissioning, such equipment shall be suitably cordoned off to prevent access.

The Contractor shall carry out touch-up painting on any equipment indicated by the Client/Consultant, if the finish paint on the equipment is soiled or marred during installation handling.

Equipment shall be installed in a professional manner so that it is plumb, square and properly aligned and oriented. No equipment shall be permanently bolted down to foundation or structure until the alignment has been checked and found acceptable by the Client/Consultant.

Consumables and Hardware

The contractor shall furnish all erection materials, hardware and consumables required for the completion of the installation. The materials shall include but not be limited to the following:

- Consumables: welding rods & gas, oil & grease, cleaning fluids, paints, electrical tape, soldering materials etc.

- Hardware: bolts, nuts, washers, screws, cable tag nails etc.

- Materials: junction boxes, terminal blocks, connectors, ferrules, lugs, brass glands, rigid/flexible conduits, cables, ground wires etc supplied by clients.

Tools, Tackles and Other Materials

The Contractor shall also furnish all necessary consumables like nuts, raw plugs, hacksaw blades, taps, dies, drills, files, wire brushes, necessary pipe scaffolding, ladders, lifting tools, wooden and consumable material like oxygen, acetylene, greases, cleaning fluids, fasteners, gaskets, temporary supports, cotton waste and all other miscellaneous supplies of every kind required for carrying out the work under the contract.

The Contractor shall not dispose, transport or take back any tools, tackles, equipment and material provided by them for the contract without taking prior written approval from Client/Consultant. Client/Consultant at all times shall have right to refuse permission for disposal, transport or withdrawal of tools, tackles, equipment and material if any, the same will adversely affect the efficient and expeditious completion of the project.

- The contractor shall provide all tools, tackle, implements, module equipment such as chain pulley block, trailers etc. which are required for transportation, handling and erection of equipment.

- Special erection tools, if any, furnished by the Manufacturer along with the equipment may be used by the contractor. Such tools and equipment, however, shall be returned in good working conditions to the owner on completion of the job.

The contractor shall also arrange for major testing equipment as list below

- Insulation Tester Motor Operated Megger 1000V & 10KV grade. Hand operated Megger 1000V.

- Hand driven earth resistance megger, range 0-1/3/30 ohms.

- Tong testers of suitable ranges.

- Contact resistance measuring set for micro-ohms.

- Torque wrench.

- Multi-meters, test lamp, field telephone with buzzer sets, different gauges etc.

- Lux meter.

- Chain pulley block, cable jacks & spindle, cable Rollers, electricians tool kit, jointer’s tool kit, fitters tool kit, welding transformer, phase sequence meter.

- Other test equipment as required for testing and commissioning of the equipment shall have to be arranged by the contractor.

Testing and Commissioning

All checks and tests as per the Manufacturer's drawings /manuals relevant code of installation and commissioning for various types of equipments shall be carried out by the contractor as part of installation work.

High voltage testing by voltage boosters, relay calibration by secondary injection, meter calibration, relay co-ordination has to be carried out at site by authorized agencies before commissioning as part of testing.

The Client/Consultant may ask for such additional tests on site to determine that the works comply with the specifications, Manufacturer's guarantee/instructions or the applicable code of installation.

The contractor shall carry out such additional tests also with free of cost.

The Client/Consultant’s authorized representative shall be present during every test as called for by the Client. The Contractor shall record all test values and furnish the required copies of the test data to the Client/Consultant. Electrical circuits and equipments shall be energized or used at nominal operating voltage only after such reports have been accepted as satisfactory by the Client.

Method of Workmanship

All work shall be installed in a first class, neat workman like manner by mechanics/electricians skilled in the trade involved.

The erection work shall be supervised by competent supervisors holding relevant supervisory license from the Government.

- All details on installation shall be electrically and mechanically correct.

- The installation shall be carried out in such a manner as to preserve access to other equipment installed.

- If in the opinion of the contractor any work is insufficiently specified or require modification, the contractor shall refer the same in writing to the client and obtain his instruction / approval before proceeding with the work.

- If the contractor fails to refer such instances, any excuse for the faulty erection, poor workmanship or delay in completion shall not be entertained.

- Equipment and material, which are wrongly installed shall be removed and re-installed to comply with the design requirement at the contractor’s expense, to the satisfaction of the owner/consultant.

- All scaffolding pipes and frames shall be of tubular steel. Bamboo/ bellies/timer frames are not permitted under any circumstances. All vertical & horizontal scaffolds shall be of MS/GI pipes of adequate size to withstand the loads & pressures. The working platforms shall be of MS bars.

Allowable Wastage

- The contractor shall make every effort to minimize wastage during erection work.

- Measurement shall be taken at site jointly by contractor and Client/Construction management representative.

- The contractor shall submit a detailed account of materials issued to them after completion of work.

- The excess materials after completion of job shall be taken back by the contractor. Contractor will raise the bill based on the actual erected material at site.

- Contractor shall clean & clear scrap material from site as per statutory requirement after installation/completion of equipment at site.

Foundation and Civil Work

- The contractor shall check the foundations provided by owner before commencement of erection to ensure their suitability.

- All final adjustments of foundation levels, chipping and dressing of foundation surfaces, drilling holes on foundation channels to suit the equipment setting and grouting of anchor bolts, sills, inserts and fastening devices shall be carried out by the contractor including minor modification of civil work as may be required for erection.

- Any cutting of masonry work which is necessary shall be done by the Contractor at his own cost and shall be made good to match the original work. The contractor shall obtain approval of owner/ consultant before proceeding with any cutting of masonry / concrete work.

Excavation and Back Filling

- The contractor shall perform all excavation and back filling as required for the scope of work specified.

- The contractor shall make his own arrangement for pumping out any water that may accumulate in the excavation.

- All excavation shall be back filled to the original level with good consolidation.

Structural Fabrication Works

All chequered plate covers, cable racks, trays, supports, hangers, anchor bolts, fasteners and brackets wherever necessary shall be supplied/fabricated by the Contactor. Steel for fabrication shall be straightened and cleaned of rust and grease. All fabrication shall be free of sharp edge.

Every effort shall be made to minimize the wastage of steel as far as practicable during fabrication. The wastage in no case shall exceed as specified elsewhere in this specification.

Approval from Electrical Inspector /Any Other Statuary Bodies

Approval of the complete electrical installation from the Govt. Electrical Inspector and or any statuary body shall be the responsibility of the contractor and the fee for the same shall be reimbursed to the contractor on submission the receipts from the Govt. dept. No other payment on this account shall be made to the Contractor. All the document support shall be provided, wherever applicable.

Repair of Damage Sustained During Transit

The contractor shall repair minor damages sustained during transit or subsequent storage in purchaser’s store. The repair charges shall be paid to the contractor based on extra work.

Inspection

After completion of erection/installation, each part of equipment shall be thoroughly tested as per approved procedure and inspected in presence of the owner/consultant for correctness and completeness of erection and acceptability for start-up.

A check list in triplicate will be furnished by the owner/consultant wherein all details to be checked and necessary instruction shall be listed. The inspection and checking shall strictly follow the checklist.

On completion of the inspection (2) copies of the check list duly filled-in shall be handed over to the Owner/consultant. This check list shall be jointly signed by the contractor and the owner/consultant. Such endorsement, however, shall not relieve the contractor of his obligations under the contract.

Handing Over and Taking Over of Works / Equipment / Systems

The Contractor shall hand over and the Client shall take over the works / equipments / systems covered under this contract only after they have been completely installed, tested and commissioned in all respects by the Contractor to the entire satisfaction of the Client / Consultant and after the said operation and all relevant test forms /certificates operation and maintenance manuals, as built drawings, etc. Incomplete / partly commissioned works/equipments/system will not be taken over by the Client. In this regard, the decision of the Client/Consultant will be final and binding on the Contractor.

Change in Quantity

Purchaser reserves the right to amend the quantities to be supplied and erected as necessary and for any such amendments, the unit rates offered by Contractor shall apply.

Actual Quantities

The Contractor shall verify the exact quantities of materials/equipments cables, etc., required after site measurements as per execution drawings by the engineer before procuring the same.

Tests

The following preliminary checks and Pre-commissioning tests shall be carried out before commissioning the Switchgears in the presence of Client/consultant’s representatives.

- Preliminary Checks

- Check name plate details according to specification.

- Check for physical damage.

- Check tightness of all bolts, clamps and connecting terminals.

- Check earth connections.

- Check the cleanliness of insulators and bushings, arc chambers.

- Check that all moving parts are properly cleaned and lubricated.

- Check if space heaters provided.

- Pre-commissioning Checks

- Check alignment of breaker trucks for free movement. Check correct operation of shutters.

- Slow closing/opening operation.

- Check control wiring for correctness of connections, continuity and values.

- Manual operation of breakers.

- Power closing/opening operation manually and electrically.

- Breaker closing and tripping time.

- Trip free operation.

- IR Values resistance and minimum pick up voltage of coils.

- Contact resistance.

- Simultaneous closing of all three phases.

- Pole discrepancy tests.

- Single and three-phase auto-reclose operation.

- Check electrical and mechanical interlocks provided.

- Check on spring charging motor correct operation of limit switches and time of charging.

- Check on CTs.

- All functional checks with the relays, meters, Alarm Scheme, interlock as per scheme with primary injection kits.

- High voltage tests on Control and Power circuits (2.5 KV)

TECHNICAL SPECIFICATION

LT PANELS

Scope includes

- Supply, unloading, testing commissioning of LT PANELS.

- Completeness of the equipment shall be the responsibility of the supplier. Any equipment, fittings, and accessories which may not be specifically mentioned in the specification or drawings, but which are usual or necessary for the satisfactory functioning of equipment (successful operation and functioning of the equipment being supplier’s responsibility) shall be provided.

- Specifically, it is a turnkey contract with sets handed over to direct use.

- All fitting and accessories or apparatus which may have not been specifically mentioned below, which are necessary and essential for the efficient working of the equipment, shall be deemed to be included in the scope.

- Transportation of LT panels at Employer’s store at site should be part of LT Panel supplier’s scope.

- Supervision of unloading of the LT panels is also to be considered in the scope.

- Arranging to repair and/or re-order all damaged and short supply items.

- Installation of panels at site.

- Supervision with Panel vendor at the time of Final check-up, testing and commissioning in presence of Employer’s representative.

- Testing commissioning and handing over to client.

LT CABLE

The specification covers design, manufacture, shop testing, packing and delivery of 1.1 kV, multi core, XLPE insulated multi strand aluminium / copper conductor armoured power cables by road/rail to the designated Store Centres in the State of Maharashtra.

All LT cables shall be 1.1 KV grade Aluminium / copper XLPE insulated, armoured cable for better current carrying capacities will be use. For lower rating from 1.5 Sq. mm to 10 Sq. mm size copper cables will be used and from 16 Sq. mm and Above Aluminium cables will be used. All wires used for point wiring purpose will be Copper, FRLS type.

General technical specification for LT cables:

- Voltage grade: 1.1 KV

- Number Of core: 4 cores up to 25 Sq. mm and above 3.5 core

- Type of insulation: XLPE insulation

- Type of Inner and outer Sheathing: PVC

- Armour: Mild steel wires, strips and tapes for armouring of cables.

- Conductor Material: Up to 10 sq. mm Copper and above aluminium

Codes & Standards LT Cable:

- IS 1554 Part-1 (1999) PVC insulated (heavy duty) electric cables for working voltages up to and including 1100V

- IS 3975 (1999) Mild steel wires, formed wires and tapes for armouring of Cables.

- IS 5831 (1984) PVC Insulation and sheath of electric cables.

- IS 8130 (1984) Conductors for insulated electric cables and flexible cords.

- IS 10418 (1982) Drums for Electric Cables.

Service conditions:

The cables shall be in all respects suitable for operation when installed:

- Indoor / outdoor in cable trays, cable ladders, wire ways, troughs and conduits / in the open air exposed to direct sunlight

- Direct buried in the ground in wet or dry locations

- In underground ducts

- Below ground in enclosed air-filled trenches, laid in cable trays

Cables shall have a design life of twenty years or more.

Cable construction:

Cable construction, conductor material, cross sectional area, number of conductors, rated voltage and cable type shall be as specified in the cable data sheets.

Cables of three or more conductors shall be assembled round with solid non hygroscopic cable fillers as needed and an overall gas/vapour-tight jacket.

All cables shall be provided with XLPE insulation.

The outer jacket of the cable shall be embossed or ink print with the following identification as a minimum:

- The voltage designation

- Number of conductors and cross-sectional area of conductors

- Type of cable

- Manufacturer’s identification.

Cable shall have uniformity in insulation and outer sheath colour.

Drum requirements:

Cables shall be drummed in maximum continuous lengths on:

Non-returnable wooden or plastic drums of sufficient strength to protect cable during shipping and handling.

Cable ends shall be sealed and fixed to the drums so that both ends are accessible. Wood legging shall be fitted around the entire periphery of the drum to protect the cable during shipment. Drums shall be suitable for long term outdoor storage at site.

All cable drums shall have the Purchase Order Number, Item Number, Drum Number and the Stock Code Number clearly stencilled in the outside of both flanges.

Drum identification labels shall be attached to the outside and inside of the drum flanges.

Labels shall be protected by transparent plastic envelopes and shall provide the following information:

- Manufacturer’s name

- Drum identification number

- Purchase order number and item number

- Cable quantity in meters

- Cable type/construction

- Cable voltage rating

- Number of conductors and cross-sectional area

- Total weight of cable and drum in Kg

- Year of manufacturing

- Stock Code Number

Cable data requirement:

The following technical particulars to be provided by cable manufacturers for each size and type of cable along with quotation:

- Standard and maximum reel lengths.

- Diameter over inner sheath

- Diameter under armour or shield

- Diameter over armour or shield

- Overall diameter of complete cable assembly

- Cable weight

- Individual conductor diameter

- Conductor DC resistance

- Conductor AC resistance

- Conductor inductive reactance

- Minimum bending radius

- Maximum conductor continuous operating temperature

- Cable current carrying capacity

- Cable short circuit withstand capacity presented in graphical form by formula

- Maximum pulling tension and sidewall loading for each conductor or cable assembly

- Descriptive literature (catalogues, etc.)

- Short-circuit current capacity of shielding tape for 0.5 second and 1.0 second fault durations.

- Maximum allowable distance for shield grounding between insulating joints to limit shield voltage to below 25 volts at full rated load.

- De-rating of cable due to circulating currents in shields.

- Power losses in cable at full current carrying capacity.

Seller to provide nominal values for typical installation methods such as tray, duct bank, individual metallic conduit in air, etc.

Conductors:

The cables shall be of solid / stranded, Aluminium / Copper conductors XLPE insulated, PVC outer sheath, galvanized steel round wire/flat strip armoured and black colour PVC overall sheathed, conforming to IS-1554 (Part- I), 1988 and 650 / 1100V grade. Multi conductor control cables shall be colour coded.

Copper / Aluminium conductor up to 10 sq. mm shall be solid, aluminium conductor, for area 16 sq. mm and above shall be of stranded construction.

Inspection & testing:

Routine test for cables as per Indian Standards shall be carried by the Manufacturer. Certified reports of all tests carried out at the works shall be furnished in six (6) copies for approval of the owner/ consultant. Cables shall not be dispatched to site unless approval shall be obtained on test certificates from Purchaser / Consultant.

Guarantee:

The cables shall be guaranteed for its successful performance and workmanship for a period of 12 months from the commissioning date.

Tests witnessed by Purchaser / Consultant will not absolve the manufacturer from overall guarantee for performance of cables.

In the event of defects during the guarantee period, vendor shall make all desirable alterations, repairs and replacement, at free of cost. The Client/Consultant shall decide whether to alter, Repair or replace & this decision will be binding on the supplier/vendor.

Packing and forwarding:

Cable length shall be supplied with +5% maximum tolerances on overall length. No negative tolerance shall be acceptable. After inspection the cable ends shall be sealed with non-hygroscopic sealing material.

The cables shall be supplied wound on non-returnable strong wooden drums of suitable diameter, width and spindle hole. All details such as cable size, type, item no., length, and drum no., gross weight of the cable shall be marked on the drum flanges. The direction of rotation of drum shall also be indicated.

Low Voltage Armoured Power Cables Data

- Cable Type 			Low Voltage Power Cable

- Voltage grade 			1.1 KV

- Conductor Insulation 		XLPE Insulated

- Insulation / Temperature 	XLPE, 90° C Dry and 70° C Wet

- Type of Inner Sheathing 	PVC

- Type of Outer sheath 		PVC

- Service 				Power distribution.

- Conductor Material Stranded 	Aluminium / copper conductor

- System Parameters 		415V, 3-phase, 50 Hz, solidly grounded,

3- Phase symmetrical fault 65kA for 1 sec at 415V

Conductor Identification

- 2-Conductors 			Red (Phase), Black (Neutral)

- 3-Conductors 			Red (Phase), Black (Neutral), Green (Ground)

- 4 /3.5-Conductors 		Red, Yellow, Blue (Phase), Black (Neutral),

- 3-Conductors with ground 	Red, Yellow, Blue (Phase), Green (Ground)

- Armour 			Mild steel wires, strips and tapes for armouring of cables

- Overall Jacket / Colour 		PVC, moisture and sun light resistant

PVC/Black

Cable installation:

Cable will be lay on cable tray, cable ladder trays partially inside and partially outside the building directly buried underground.

Cables shall be laid in a continuous length. The cables shall be handled carefully. In order to avoid undue tension and damage to the cable, it shall be unwound by means of jacks and rollers. While laying cables, care shall be taken so that its route shall be not obstructed by other services, and it does not rub against sharp edges. Each run of the cable shall be measured before cutting the cable from the drum. Cables shall be neatly dressed, clamped on fully / partly supported horizontal run and vertical run. Bending radius of HT cables shall not be less than 15 times the overall diameter of cable. Bending radius of LT cables shall not be less than 15 times the overall diameter of cable. Care shall be taken during laying to avoid sharp bending and twisting. Cable shall be unwound from the drum by lifting the drum on the centre.

This shall also be considered while unwinding the cables from drum. Armoured cables shall be terminated with single compression / double compression / flameproof cable glands. Cables armour shall be securely clamped and bonded to body of gland. Armour shall be properly cleaned, and petroleum jelly shall be applied to armour and clamping surface.

On the ground cable can be flaked in a figure of eight formation, do not attempt “coiling” of cable on the ground.

Approximate lengths of cables run will be given in the cable schedule. Before procurement the Contractor shall take actual measurements and prepare his own cable cutting/drum schedules to reduce wastage to a minimum. The Contractor shall also maintain and submit when requested, a record of cable insulation value when drawn from store, after laying, before and after termination/jointing.

Storing

On receipt of cables at site, cables shall be inspected to detect any damage.

The ends of cable shall be in sealed condition. After inspection, cable shall be located in a proper place with battens of cable drums being replaced. The cable drums shall not be stored 'on flat' with flanges horizontal.

Client/Consultant will inspect the cables before storing. Contractor shall take out samples from the drums as per their instructions and send them to the manufacturers to conduct the approval tests. After the receipt of the test analysis, the cable will be accepted by the Owner.

Cables and Cable Entries

Particular attention is drawn to the Contractor’s responsibilities in safeguarding cables installed in outdoor locations and unfinished buildings. Such equipment is particularly vulnerable to damage from water and dust penetration. The Contractor shall ensure that cables are adequately protected in this respect while installation work is proceeding. Covers temporarily removed from trenches/entries for purpose of installation shall be reassembled on completion of the Work and replaced when such work is suspended or otherwise left incomplete. Similarly, all entries shall at times be effectively sealed against ingress of water and dust, eg. Duct entries shall be sealed by the insertion of proprietary stopper plugs or approved means.

Storage and Handling of Cables

Storage & handling of cable before and during installation shall be executed with regard to Manufacturer’s recommendations. Cable drums shall be rotated only in the direction indicated on the drum, and open ends of cable shall be effectively sealed after cutting to prevent ingress of moisture, using heat shrink end caps.

- Cable drums shall be stored on hard and well drained surface so that they may not sink. In no case the drum shall be stored on the flat i.e., with flange horizontal.

- Rolling of drum shall be avoided as far as practicable. For short distance, the drums may be rolled provided they are rolled slowly and in proper direction as marked on the drum.

- In absence of any indication the drums may be rolled in the same direction as it was rolled during taking up the cable.

- For unreeling the cable, the drum shall be mounted on jacks or on cable wheel. The spindle shall be strong enough to carry the weight without bending.

- The drum shall be rolled on the spindle slowly so that cable should come out over the drum and not below the drum.

- While laying cable, cable rollers shall be used at an interval of 2000 mm. The cable shall be pushed over the roller by a gang of people positioned in between rollers.

- Cable shall not be pulled from the end without having intermediate pushing arrangement. Bending radius of the cable shall not be less than that is specified by the manufacturer.

- All possible care shall be taken during unreeling and laying to avoid damage due to twist, kink or sharp bends.

Cable Pulling

Armoured cables shall be installed with the aid of specifically manufactured rollers, in order to prevent damage to outer sheaths. Cables up to 38 mm diameter shall be installed by hand. However, larger cables, with the approval of the Company Site Representative, may be installed with the assistance of a winch. Any such winch shall be equipped with a suitable tensioning device and indicator and operated by a competent operator.

Cable shall never be installed directly from a drum mounted on a moving vehicle.

Drum jacks, cable rollers and other equipment shall be of the correct type for the cable being installed.

Recommended safe pulling force with stockings

a) For Unarmoured Cable: P = 5 D2

b) For Armoured Cable: P = 9 D2

Where P = Pulling Force

Where D = Diameter of cable in mm

Cable Bending

At all times almost care shall be exercised to prevent excessive bending or twisting of cable during installation. Changes in direction in cable trenches, racks or trays shall provide for a minimum cable bending radius of 15 times the overall cable diameter.

Cable Jointing

Cables shall be run in continuous unbroken lengths. Any requirement for cable jointing shall be executed only with the approval of the client/consultant representative.

All cable jointing shall be executed by fully trained tradesmen who have passed an approved course of instruction in such work for the operating voltage level concerned. Written confirmation in this respect shall be furnished to the Company Representative by the Contractor.

Protection from Moisture

Each cable system shall be installed either where it will not be exposed to rain, dripping water, steam, condensed water, etc., or be of a type designed to withstand such exposure.

In damp situations and wherever they are exposed to weather, all metal sheaths and armour of cables, metal conduit, ducts, ducting trunking clips and their fixings, shall be of corrosion-resistant material or finish, and shall not be placed in contact with other metal with which they are liable to generate electrolytic action.

For conductors insulated with impregnated paper, exposed conductor & insulation at terminations and cable joints shall be protected from ingress of moisture by being suitably sealed.

Cable Lying

- Cable shall generally be installed in ladder type / perforated trays in trenches/pipe racks or buried in ground except for some short runs in conduit for protection or crossings the roads etc.

- Each length of run shall be physically measured at site before cutting the cable. Contractor shall furnish cable cutting schedule to engineer in charge with respect to able drum length available at site and runs of cables & sizes of cables.

- Cable may also be laid through Hume pipes/corrugated high density PVC pipes (as approved by the consultant/owner) in road crossings etc. The pipes shall be supplied and placed in position by the Contractor.

- Cable laid on trays and risers shall be neatly dressed and clamped at an interval of 2000 mm and 500 mm for horizontal and vertical cable run respectively and at each bend of cable.

- All power cables shall be clamped individually, and control cables shall be clamped in groups of three or four cables.

- Clamps for multi-core cables shall be fabricated of 25 x 3 mm G.I. flats. Single core power cables shall be laid in trefoil formation and clamped with trefoil clamps made of Fiber glass/PVC.

- Cable openings etc. in walls/floor made by the Contractor or by others shall be sealed by the Contractor suitably by Hessian tape and bitumen compound or by any other proven method to prevent ingress of water.

- Directly buried cables shall be laid as per detail shown in drawing. These cables shall be laid on and covered with sand / raddle earth and protected by brick barriers as sides and precast concrete slab brick on top. Job also involves digging/excavation of earth and refilling the same after laying of cables. For cables laid underground a loop of diameter of 3 meters shall be provided near each terminating ends.

- After completion of installation and prior to connection, all High Voltage Power cables shall be given a high potential test. The contractor shall provide this Hi pot Test set having provision of leakage current measurement.

- Laying cost shall include all above activities excluding supply of clamps but including cable tag at every 20-meter interval etc.

Cable Termination

- All work on the termination of cables shall be executed by fully trained & competent tradesmen who have passed an approved course of instruction in such work for the operating voltage level concerned. Written confirmation in this respect shall be furnished to The Company Site Representative by the Contractor.

- The cable termination includes drilling of Gland plate as require size of the cable and no. of cables in each section/cable alley.

- The termination, Joints and connections of cables shall be done by qualified jointers strictly in accordance with manufacturer’s instruction drawings and/or as directed by the Engineer

- The work shall include all clamping, fittings, fixing, plumbing, soldering, taping, compound filling, epoxy cable jointing, crimping, connecting, shorting and earthing as required for all such operations should be available with concerned contractor. For all size of LT termination, crimping tool (Hydraulic type) shall be used. Further, inhibiting compound shall be provided before termination.

- The equipment will be generally provided with blank plates for cable/conduit entry and cable end box for power cables.

- The Contractor shall perform all drilling, cutting on the blank plates and any minor modification work required to complete the job.

- If the cable-end box or terminal enclosure provided on the equipment is found unsuitable and requires major modification, the same shall be carried out by the Contractor as extra work item.

- Control cable cores entering control panel / switch gear /PCC/ MCC etc. shall be neatly bunched and served with nylon cord or PVC perforated tape to keep in position at the terminal block.

- The contractor shall provide oil resistance ferrules for all control cable cores at all terminations including at all junction boxes and at all terminations. The ferrules shall carry terminal numbers as per drawing. The ferrules shall be of interlocked plastic type or approved equal.

- Spare cores shall be similarly tagged, crimped with lug and taped on the ends. Spare cores shall be tagged with individual cable number.

- Terminations and connections shall be carried out in such a manner as to avoid strain on the terminals.

- All cable entry points shall be sealed and made vermin and dust proof. Unused opening, if any shall be effectively closed.

- All connections at a cable termination shall be mechanically & electrically sound and shall be protected against mechanical damage or any vibration liable to occur. They shall not impose any appreciable mechanical strain on fixing of the connection and shall not cause any harmful mechanical damage to the cable conductor or equipment. Conductors of cables shall be terminated in a manner suitable for the terminal arrangement of the equipment concerned.

Glands, Seals and Shrouds

- The entire body of a cable shall enter a gland, & the outer sheath of a cable shall not be removed before entering the weatherproof seal. Cable shall be on a straight axis from a point immediately before entering a gland.

- Cable glands shall securely retain the cable without damage to the outer sheath or armour.

- Glands shall be correctly sized and of a type suitable for installation in each respective type of enclosure.

- All glands shall be correctly sized and of a type which will maintain the integrity of the equipment within into which they are to be installed. Such factors as use of insulated plastic enclosure and explosion proof type protection shall be taken into account when selecting glands. Mechanical glands shall be of the hexagon double compression type, knurled type glands shall not be used.

- Earth continuity of brass glands & terminations shall be achieved by rigid clamping of armour within each gland and intimate contact between threaded components of glands and equipment.

- Brass glands terminating in unthreaded enclosures shall be provided with earth continuity by attachment of earth continuity bonds.

- Terminations of mineral insulated cable shall be provided with sleeves having a temperature-rating equal to that of the seals.

- Cores of sheathed cables, from which the sheath has been removed, and non-sheathed cables at terminations of conduit, ducting or trunking, shall be enclosed according to the design specification.

Terminal Connecting Lugs

- Cable tails of conductors shall be fitted with compression-type terminal connection lugs, using tools specially designed for use with such lugs.

- At all terminal connections, cable conductors shall be fitted with correctly sized cable sockets of the crimped compression type. Soldered connections shall be employed only where their use is unavoidable. Solder used shall have a melting point of not less than 185 Deg C, and cable lugs or thimbles shall be the correct type and size for each conductor. Packing of oversized lugs shall not be permitted.

- Compression joints shall be made using proprietary sets of lugs and indent dies, correctly sized and shaped for each specified conductor concerned. Use of mixed lugs and dies of different manufacture or systems shall not be permitted.

Sealing of Cable Transits

- Openings made or provided in or through building walls, floors, etc., shall be effectively sealed.

- Cable entries into trenches (in switch rooms, etc) shall be effectively sealed after cables have been laid. Unused cable entries and cable entries in equipment also shall be effectively sealed.

- Openings through roofs and external walls shall be made weatherproof, including installation of flashing and / or rain hoods to prevent the entry of driving rain, seepage of water, dust, etc.

Cable Supports

- Every cable and conductor used as fixed wiring shall be supported in such a way that it is not exposed to undue mechanical strain and so that there is no appreciable mechanical strain on the terminations of the conductor. Account shall be taken of the mechanical strain imposed by the supported mass of the cable or conductor.

- Conduit, ducting and trunking shall be properly supported and of a type that is either suitable for any risk of mechanical damage which may be met in normal conditions of service, or adequately protected against such damage.

- Installation shall consider longitudinal expansion and contraction that may occur with variation of temperature under normal operating conditions.

Cable Tags and Markers

- Each cable and conduit run shall be tagged with numbers that appear in the cable schedules.

- Cables and conduits shall be tagged at every twenty (20) meters. Cables and conduits shall also be tagged on either side of a floor/wall passage.

- The tags shall be of Aluminium with the number engraved on it and securely attached to the cable by not less than two turns of PVC tie.

- Location of cables laid directly underground shall be indicated clearly by cable marker made of cast iron.

- The location of cable joints, if any, shall be clearly indicated with cable marked with an additional inscription “Cable Joint”.

- The marker shall project 200 mm above ground and shall be spaced at an interval of 20 meters at every change of direction.

- Cost of laying shall also include supply and fixing of tags, cable markers etc.

Testing

Cables shall be tested at site as follows:

- Before shifting of cables drums from the yard to the site, insulation resistance shall be carried out on the cable and readings recorded in the presence of the Site Representative.

- On cable being laid prior to sand bedding an I.R. shall conducted and recorded in the presence of the Site Representative.

- On the cable trench route being completed and compassion done an I.R shall be conducted and recorded in the presence to the Site Representative.

- No backfilling of trenches shall be done till the trench/sand padding/ cables are inspected and tested.

- Before end terminations are made an I.R shall be conducted to ensure the cable is in order.

- On termination’s being completed prior to connecting to the equipment. The following test shall be conducted.

  - An I.R. done on the cable/Termination.

- Cable/term subject to a pressure test for 15 minutes. The voltage to be applied shall be as per manufacturer’s recommendations and in co-ordination with Owners/Consultants.

- An I.R. Done on completion of the above Hipot test. All tests shall be done and recorded in the presence of the Site Representative.

POINT WIRING, MAINS WIRING, CONDUITS, & ACCESSORIES

General

The wiring installation shall confirm to IS: 732-1963 latest addition.

For any type of wiring PVC pipes shall be used. Minimum size of conduits used for any type of wiring, in shall be at least 20 mm. diameters.

Multi-stranded copper wire of 1.5 / 2.5 / 4 sq.mm. Copper wire with 1.1 KV graded shall be used.

Wiring in office area, canteen and toilets will be concealed in concrete structure or above the false ceiling or below floor. PVC conduits, raceways, cable trays shall use for the basic routes for the wiring.

All the point wiring will be done using FRLS wires.

Standard colour code shall be used for wiring. Coloured insulated wire of respective colour shall be used for phase conductor and black colour insulated wires shall be used for neutral conductor and green colour wire used for Earthing conductor.

The wiring shall be done in looping system. The phase conductor shall be looped at the switch box for sub-circuits. No bare wires shall be used for interconnection of switches.

The wiring conductors shall not be drawn into the conduits until all the works of any nature that may cause damage to the wires are completed. The installation and termination of wires shall be carried out with due regard to the followings.

- While drawing the wiring conductors, care shall be taken to avoid scratches and kinks which cause breakage of conductors. There shall be no sharp bends in the conduit system.

- Insulation shall be shaved off like sharpening of a pencil and it shall not be removed by cutting it. PVC insulated copper conductor shall be soldered at the ends. Strands of wires shall not be cut for connecting terminals. The terminals shall have sufficient cross-sectional area to take all strands and shall be soldered.

- Oxide inhibiting grease shall be applied at all terminals and connections.

- Connecting brass screws shall have flat ends.

- Brass flat washers of large area shall be used for bolted terminals.

- Bimetallic connectors should be used wherever aluminium conductors are tapped from copper mains or vise versa.

- All looped joints shall be soldered and connected through terminal block/ connectors.

- The pressure applied to tighten terminal screws shall be just adequate (neither too much nor too less). Conductors having nominal cross-sectional areas exceeding 10 Sq.mm shall always be provided with cable sockets.

- All wires and cables shall bear the manufacturer’s label and shall be brought to site in original packing.

- For all internal wiring, PVC insulated wires of 650/1100 volts grade shall be used.

- The sub-circuit wiring for point shall be carried out in loop system and no joints shall be allowed in the length of the conductors.

- Before the wires are drawn into the conduits, the conduits shall be thoroughly cleaned of moisture, dirt of any other obstruction by forcing compressed air through the conduits.

- The minimum size of PVC insulated conductor wires for all circuit wiring/Cable for light points shall be 2.5 sq.mm& for socket outlet shall be 4.0 Sqmm.

- Separate conduit shall run for LAN wiring and the same shall not run in parallel to power wiring conduit.

- Strands of the wires shall not be cut for connecting to the terminals or lugs. The terminals shall have adequate cross section to take all the strands.

  - Wiring for power and lighting circuits shall be carried out in separate and distinct wiring systems.

  - Wires carrying current shall be so bunched that the outgoing and return wires are drawn into the same conduit. Wires originating from two different phases shall not run in the same conduit.

  - The incoming cable size from MLDB to DB shall be as indicated in the respective SLDs/lighting layout drawings.

  - The wiring system envisaged is generally shown on the layout drawings and line diagrams. However, a brief account of the general wiring system is given below:

  - Circuit Wiring (Main Point) – Circuit wiring shall means the wiring from Distribution boards to the 1st Tapping point inside the Switch box from where point wiring starts and inside the first socket outlets and shall consist inclusive of supply & installation of wire, conduits along with conduit accessories, pull wire wiring, pull boxes, junction boxes, as required and specified. The sizes of conduits and number of wires shall be as specified in Schedule of Quantities. Wires shall be drawn in conduits as required without being damaged, with necessary draw boxes if required. The wire lengths must be adequate for terminating at either end or identifying ferrules shall be provided at termination. The wiring shall be colour coded. The rate shall include all materials, connections, labour etc. as specified above.

  - Point wiring – point wiring (other than socket outlets point) shall include all work necessary in complete wiring to the following outlets from the controlling switch or MCB

- Primary Point wiring means the wiring from the Switch box/MCB to the 1st tapping point (first light fitting).

- Secondary point wiring means the wiring from the 1st tapping point (first light point) to 2nd tapping point ( Second light point )

- The scope of work shall be same as in Circuit wiring.

  - Power wiring: The wiring from DB’s to Power plug wiring for 16A single phase industrial plug & sockets and 32A three phase industrial plug & sockets shall also be carried out in recessed/surface MS conduit. The scope of work shall be same as in Circuit wiring.

  - Looping wiring: - Looping wiring means the wiring from the switch box to the 1st tapping point inside the switch box, from where point wiring starts.

  - Point wiring shall commence from the first point control box/local control box for the points connected to the same circuit. Point wiring for lights, ceiling and exhaust fans, etc. shall be carried out with 1100 V Grade PVC insulated wires. The point wiring shall be inclusive of supply & installation of conduits along with conduit accessories, pull wire, wiring , pull boxes, junction boxes, , covers etc. together with wiring accessories such as ceiling roses wires up to 1000 mm long at outlet end connectors point control boxes (enclosure for electrical accessories) switches, etc. Point wiring shall be installed with earth continuity wire as specified for Earthing 3rd pin of sockets, luminaries and fan fixtures. Light control shall be either single, twin or multiple points controlled by a switch, as specified.  The point wiring for Light/Fans/5A sockets etc. shall include supply of all material & labour job. The fan point shall be complete with fan hook box flush mounted in slab complete with cover. The measurement will be numbers of each kind of point and as specified in Schedule of Quantities.

  - Each circuit main/power wiring/point wiring/looping circuit shall also have its own earth continuity wire as specified.

  - All the wiring shall be carried out in loop-in-loop system only and phase or line conductors shall be looped at switch box and neutral conductor can be looped from light, fan or sockets.

  - The maximum number of various size conductors that could be drawn into various sizes of conduits shall be as per table II of IS: 732 (Latest Edition). The wiring shall be colour coded for easy identification of phases and neutral. The following colour codes shall be adopted.

    - Phases - Red, Yellow and Blue.

    - Neutral - Black.

    - Earth - Green or Bare wire as specified.

  - All circuit wiring/point wiring shall be provided with printed PVC identification ferrules at either end bearing the circuit number and designation.

Maximum permissible numbers of 650/1100 volt grade PVC insulated wires may be drawn into rigid conduits are as below:

| Size of Wire mm2 | Size of conduit mm |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Nominal Cross sectional area | 20 | 25 | 32 | 40 | 50 |
| 1 | 7 | 13 | 20 |  |  |
| 1.5 | 6 | 10 | 14 |  |  |
| 2.5 | 5 | 10 | 14 |  |  |
| 4 | 3 | 6 | 10 | 14 |  |
| 6 | 2 | 5 | 9 | 11 |  |
| 10 |  | 4 | 7 | 9 |  |

Conduit Installation

MMS grade FRLS PVC conduit shall be used for electrical installation.

The inside surface and ends of conduits and threads and fittings used shall be clean, smooth, cut square and free from burrs and other defects

The conduit shall be properly and tightly screwed between the various lengths and to the boxes to which it runs and terminates. No part of the conduit shall be under mechanical stress and the whole conduit system shall be mechanically continuous throughout.

All jointing methods shall be subject to the approval of the Consultant/Client. Separate conduits shall run for all power outlet wiring.

The joints in conduits shall be free of sharp edges to avoid damage to insulation of conductors while pulling them through the conduits.

Where necessary, bends or diversions may be achieved by means of bends and/or circular inspection boxes with adequate and suitable inlet and outlet screwed joints. In case of recessed system each junction box shall be provided with a cover properly secured and flush with the finished wall surface. No bends shall have radius less than 2-1/2 times the outside diameter of the conduit

All conduits shall be installed as to avoid contact with hot surface. After the conduits, junction boxes, outlet boxes and switch boxes are installed in positions, their outlets shall be properly plugged or covered so that water, mortar, insects or any other foreign matter does not enter into the conduit system. Surface conduits shall be fixed by means of space bar saddles at intervals not more than 500 mm.

Installation of Recessed Conduit System

The conduits shall be installed in such a manner that running can be carried out from the fitting boxes and switch boxes only.

Conduits which are to be taken in the ceiling slab shall be laid on the prepared shuttering work of the ceiling slab before concrete is poured, and tied to bars at every 750/900 mm. The conduits shall be made water-tight by using bituminous compound at the joints. The conduits in ceiling slab shall be straight as far as possible.

Conduits recessed in walls shall be secured rigidly by means of steel hooks/staples at 500 mm intervals. Before conduit is concealed in the walls, all chases, grooves shall be neatly made to proper dimensions to accommodate the required number of conduits.

The outlet boxes, point control boxes, inspection and draw boxes shall be securely fixed by means of counter sunk steel screws and raw plugs. They shall be firmly grouted in position prior to plastering fixed as and when conduit is being laid. The recessing of conduits in walls shall be so arranged as to allow at least 12 mm plaster cover on the same. All grooves, chases, etc. shall be refilled with cement mortar and finished up to the wall surface before plastering of walls is taken up by the general contractor. The top edge of the conduit shall be at least 25 mm below the finished surface of wall.

After conduits, junction boxes, outlet boxes, etc. fixed in position their outlets shall be properly plugged with PVC stoppers or with any other suitable materials so that water, mortar, vermin’s or any other foreign material do not enter into the conduit system.

To facilitate easy drawing of wires in conduit necessary GI pull wires of 16 SWG shall be inserted into the conduit immediately after shuttering is removed.

The Electrical Contractor shall be present during the pouring of concrete to ensure that the conduits and accessories are not displaced or blocked.

The conduits shall be swabbed out by drawing dry swabs of rag through the conduit to remove all moisture prior to drawing of wires.

Where vertical concealed conduits pass through floors or beams and horizontal concealed conduits required to pass through columns or beams, these shall be taken through rigid PVC/GI pipes to be inserted in the floors /columns/beams, etc. during casting for which no extra payment shall be entertained.

Extension collars of suitable depth shall be used as necessary to leave all boxes absolutely flush with the finished wall or ceiling surface.

Conduits shall not be buried or plastered etc. unless and until the work has been inspected by the Client/ Consultant.

Installation of Surface Conduit System

Conduits shall run in square and symmetrical lines. Before the conduits are installed, the exact routes shall be marked at site and approval of the Consultant shall be obtained. Conduits shall be fixed by heavy gauge GI base plates, saddles, secured to suitable raw plugs, at an interval of not more than 500 mm. Conduits shall be joined by means of screwed couplers and screwed accessories only. In long distance straight runs of conduit, inspection type couplers or running type couplers or pull boxes shall be provided.

Bends in conduit runs shall be done by bending conduits by pipe bending machine. Bends which cannot be negotiated by pipe bends, shall be accompanied by introducing inspection boxes or inspection bends. Not more than three equivalent 90 C bends shall be used in a conduit run from outlet to outlet.

All the conduit openings shall be properly plugged with PVC stoppers/bushes. The conduits shall be adequately protected against rust by applying two coats of approved synthetic enamel paint after the installation is completed.

Wherever conduits terminate conduits shall be rigidly connected to the box/board with brass hexagonal check nuts with compression washers on either side of the entry to ensure proper electrical and mechanical continuity.

The crossing of surface conduits shall not be generally permitted and to avoid such crossings, adopter boxes shall be used at junctions/crossings.

All unused conduit entries shall be blanked off in an approved and where a conduit terminates in adopter boxes. All removable box covers shall be firmly secured to provide complete enclosure

Conduits above False Ceiling

In the false ceiling area, the conduits shall be run above the false ceiling frame work supported by means of M.S/GI strips secured and fixed to both conduits and structural ceiling, keeping the outlet box as near as possible to the fittings/fans for connections. The conduit boxes for fittings/fans are independently supported by means of separate fixing arrangements to the box and structural ceiling so that the box is held rigidly.

Modular switch & socket & accessories, surface/concealed box.

Unless specified the switchboards switch sockets and its accessories shall be readymade type as per make mentioned in approved make list attached to the tender document.

- At least one earth stud is a must.

- Minimum depth 60 mm.

- All switches and sockets shall confirm respective I S.

- All switches shall be of approved make.

- Ceiling roses shall be 3 plate types.

EARTHING SYSTEM

Earthing electrodes shall be designed as per the requirements of IS 3043 Earth pits shall be further treated with earth conductivity enhancing mineral compound tested as per IEC 62561-7 shall be supplied by Contractor. All non-live metal parts of the electrical system and equipment shall be earthed with suitable size of earth conductors. Two distinct earthlings shall be provided for all the equipment. All earth Pits shall be located 2.0 Mtrs. away from the building and there will be a minimum distance of 2.4 Mtrs. Between two earth pits.

Equipment earthing shall be carried out as per the installation details- Earthing and the System earthing as per layout drawings. All connections to earthing stations shall be checked and the loose connections shall be tightened to get good continuity of ground circuit. Ground pits shall be installed as per the Installation details- earthing, Ground resistance at every ground pit and plant building shall be checked by opening the test link provided, and with the help of a good quality kit supplied by the contractor.

The equipment earthing materials shall be G. I./ CU strip of adequate cross section as indicated in Installation details- earthing. The drilling and cutting of GI. Material shall be carried out before galvanizing. Wherever drilling and cutting shall be carried out after hot dip galvanizing, the affected area shall be tinned to prevent corrosion. Two ground terminals will be provided on the electrical equipment. However, if these are not available, the contractor shall provide the same by drilling and tapping the same with necessary hardware. The cable armour shall be bonded to ground at both ends through cable glands.

Joints and tapings in the main ground loop shall be made in such a way that reliable and good electrical connections are permanently ensured. All joints below grade shall be welded and suitably protected by giving two coats of bitumen and covering with adhesive tape. All joints above ground shall be by means of connectors / lugs as far as practicable. Tee connectors shall be used for tapping; ground leads from the main ground loop wherever it shall be installed above ground. It shall be provided for earthing of two or more equipment at a place from ground grid. Copper lugs shall be used for cable termination. The GI. Riser shall be protected by applying two coats of bituminous paint / bitumen on the exposed portion.

Earth station

- Pipe electrode earthing

65 mm. diameter.GI. Pipe of 6.0 Mtrs. long provided with 12 mm. diameter Holes at 75 mm. C/c on all sides for bottom 2.0 Mtrs. With 50 x 6 GI strip connected from top to bottom, top side watering arrangement shall form earth electrode. The electrode has to be buried vertically in ground.

- Masonry chamber

Brick masonry chamber of size 600 x 600 x 450 mm. Minimum (internal clear dimensions) with RCC cover and frame with top finished at ground level shall be provided for watering and test link.

- Artificial treatment

In case of rocky soil, hard murum soil resistance is very high. For getting proper earthing alternate layers of bentonite and black soil with 300 mm. Overall cover shall be provided.

- Earthing conductors.

The earthing conductor shall be connected

GI Flat conductor, with welding at all the joints with 2 coat of bitumen paint.

CU Flat conductor, with Brazing at all the joints.

Earthing conductors for lightening protection shall run on parapet walls of outer periphery of building and on unapproachable vertical walls up to disconnecting box fixed at 1.0 Mtrs. high above ground level. Lightening conductor shall be connected to earth station directly and separate 50 x 6 mm. strip from earth station is to be connected to the grid earthing.

All switch boards, socket outlets and lighting fixtures shall be earthen with suitable size of FRLS copper wire as per BOQ, with proper ring type lug at both ends,

All earthing wires shall be connected to the earth bus provided near the distribution board.

Inspection & testing

Following tests shall be taken after installation of earthing conductors and Earth Pit.

- Cable continuity.

- Earth conductor continuity

- Insulation Resistance Tests Using 1000v DC Megger Earthing.

Typical Bore earthing PIT details

LADDER & PERFORATED TYPE CABLE TRAY

All materials and hardware supplied shall be new, unused and of best quality and shall conform to the latest specifications & Standards. Cable trays and Fittings shall be ladder & perforated type GI. with natural mill finish &Corrosive resistant type. These trays shall consist of side rails and horizontal rungs.

Ladder type cable trays and fittings shall be heavy duty type. The ladder type trays shall consist of side rails and horizontal ladder rungs of slotted channel type. The side rails shall be formed to channel shape of 17mm depth. All corners shall be smooth. The spacing between ladder rungs shall be 300mm. The rungs shall be welded / bolted to side rails as per manufacturer’s standard. Side rails shall have 10mm dia. holes at each end of straight sections, elbow crosses etc. for fixing side couplers.

The side rail channel shall have four holes on each end for fixing coupler plates. Two coupler plates (on outside face) shall be provided for each side runner. Suitable threaded holes shall be provided on the runner for supporting and fixing tray covers with hardware at every meter. The type of construction shall be such as to facilitate easy handling, assembly and installation at site. The cable tray shall be in the Manufacturer’s standard lengths. All surfaces shall be free from defects from manufacturing such as burrs, sharp edges, etc.

The hardware shall conform to the relevant standards and shall be able to withstand the maximum loading conditions as required. All cable tray hardware such as nuts, bolts etc. shall be with electro zinc plated steel. All cable tray and fittings shall be supplied along with coupler plates and the Manufacturer’s associated hardware. Manufacturer’s standard self-adhering warning label of black letters on white background with following information shall be provided on cable trays.

DATA NETWORK SYSTEM

- Data cabling from hubs /Jack panel switches to RJ 45 LAN sockets is proposed with CAT 6 E UTP cable in 20/25mm  dia PVC conduit (concealed wiring) / MS conduit (open wiring) & Alum. Trunking.

TECHNICAL SPECIFICATIONS

MAKES OF MATERIAL

| CABLES HT | POLYCAB, FINOLEX, RR CABLE, RAVIN, KEI, HAVELLS |
| --- | --- |
| CABLES LT | POLYCAB, FINOLEX, RR CABLE, RAVIN, KEI, HAVELLS |
| GLAND FLENGE TYPE | EMI, HMI |
| LUGS | DOWELLS, COMMET |
| HT SWITCH GEAR | SIEMENS, SCHNEIDER, ABB, CG, L&T |
| HT CABLE TERMINATION | RAYCHEM, M SEAL |
| LT SWITCH GEAR | SIEMENS, SCHNEIDER, ABB, L & T, LEGRAND |
| TRANSFORMERS | VOLTAMPS, KIRLOSKAR, RAYCHEM RPG, UNIVERSAL, CG, MAHATI |
| DG SET | CUMMINS, KIRLOSKAR, CATER PILLER, STERLLING, MAHINDRA POWEROL, |
| UPS | NEOWATT, EMERSON, APC, ADOR, HITACHI, EATON, NUMERIC |
| BUSBAR SYSTEM | SIEMENS, SCHNEIDER, L&T, C&S, & LEGRAND, GODREJ, POWER BAR |
| LT POWER CONTACTORS | SIEMENS, SCHNEIDER, ABB, L & T |
| CAPACITORS | SIEMENS, SHRIM, VISHAY, SUBODHAN, L&T |
| ACB'S | SIEMENS, SCHNEIDER, ABB, LEGRAND, L&T |
| MCB’S AND MCB DB’S | SIEMENS, SCHNEIDER, ABB, LEGRAND, L&T |
| MCCB’S AND MCCB DB’S | SIEMENS, SCHNEIDER, ABB, LEGRAND, L&T |
| PVC CONDUIT | PRECISION, DIAMOND, BEC, VIMCO |
| M S CONDUIT | BEC |
| WIRES | POLYCAB, FINOLEX, RR, HAVELLS, KEI. |
| TELEPHONE CABLES | POLYCAB, FINOLEX |
| DATA CABLE (CAT 6) | D LINK, AMP, LEGRAND, POLYCAB, SYSTIMAX |
| SWITCHES, SOCKETS | ANCHOR, SCHNEIDER, LEGRAND, L&T, ABB |
| TELEPHONE SOCKETS | ANCHOR, SCHNEIDER, LEGRAND, L&T |
| CEILING ROSE | ANCHOR, SCHNEIDER, LEGRAND, L&T |
| LIGHTING FIXTURES | WIPRO, PHILIPS, GENERAL ELECTRICALS, BAJAJ, CROMPTON GREAVES, |
| CEILING FANS | CROMPTON, GEC, BAJAJ, PHILIPS, HAVELLS |
| EXHAUST FANS | CROMPTON, GEC |
| LT PANELS | CPRI APPROVED PANELS AS PER IEC 60439 |
| CABLE TRAYS | PROFAB, IDIANA, LCON |