## Heat Pump Description
Description of the proposed HEAT PUMP SYSTEM to be installed.
Supply Installation, Testing and commissioning of Heat Pump system considering the hot water requirement of 12000 liters for a period from 6.00 am to 11.00 am and from 6 .00 pm to 8.00 pmincluding hot water tanks, Heat pump systems, Electrical and mechanical systems required to be installed for trouble free operations of the Heat Pump with a battery limit of inlet to the Tanks and out let connected to the Main Supply Pipe ring installed on terrace and bringing back from the return pipe ring installed on the terrace. The temp rise expected is from 20 Deg Cel to 55 Deg Cel. The storage tanks proposed are insulated pressurized tanks of 3000 ltrs capacity 4 nos .
The capacity is worked out as follows.
§ No of Total Beds 250 Beds.
§ ICU Beds 80 Nos.
§ Pvt. Rooms 60 Nos.
§ General Beds 110 Beds.
Hot Water shall be supplied only from 6.00 am till 11.00 am. And from 6.00 pm to 8.00 pm
Hot Water Requirement
ICU Beds 80 Nos. 7 Liters per Bed (Only Sponging) = 560 Liters
Pvt. Rooms 60 Nos. 50 Liters (Shower Bath) = 3000 Liters
General Beds 110 Beds. 30 Liters (Bucket Bath) = 3300 Liters
Nursing Stations / Scrubbers / OT’s ; Total requirement(24 X 7 Hot Water Requirement) ( for round the clock requirement, decentralized on Line Water heaters will be used. ) = 2000 Liters
Spare Capacity as directed by the Hospital Management = 3000 Liters
Total Hot Water requirement = 11860 liters… say 12000 Liters

## Specifications & Data Sheets
Technical Specifications for Heat Pump - Air - Water
A | Heat Pump | Unit | SPECIFICATIONS | Quantity | VENDOR TO SPECIFY
1 | Model No |  | Please Specify
2 | HP Rated Power (Input) | kW | 4
3 | HP Rated Heating Capacity (Output) | kW | 16.5 | 4
4 | COP - With Fan & Circulation Pump |  | Minimum 3.8 (To be Tested)
5 | Power Supply |  | 415 V/3/50
6 | Hot Water Capacity | LPH | 475 - 385
7 | Maximum Water Outlet Temprature | 0C | 55
8 | Operation Temprature Range | 0C | 15-60
9 | Ambeint Temprature for HP | 0C | 10 - 40
10 | Unit Operation Noise | dB(A) | Less than 60
11 | Compressor Make |  | EMERSON/ DANFOSS
12 | Compressor Type |  | SCROLL
13 | Compressor Quantity | Nos | Please Specify
14 | Fan Quantity | Nos | Please Specify
15 | Condensor Type |  | PLATE TYPE HEAT EXCHANGER
16 | Refrigerant to be used |  | Eco Friendly - R-407 C or R 134 A
17 | Condensor Make |  | SWEP / ALPHA LAVAL
18 | Cabinet Type |  | 18 gauge Galvanized MS Sheet to be powder coated.
19 | Cabinet Colour |  | As per Vendor's Design
20 | Working Pressure | kg/cm2 | FOR GAS HIGH SIDE PRESSURE 430 PSI (~30.5 kg/cm2)/ LOW SIDE PRESSURE 90 PSI (~6.5Kg/cm2)/
21 | Testing Pressure | kg/cm2 | Copper Tubing Leak Testing Pressure 500 PSI (35.15 kg.cm2) Rated Bursting Pressure of Copper Tubing 3000PSI
22 | Circulation Pump Make - 1 W + 1 S By for Each Heat Pump with Automation |  | Specify
23 | Pump HP | kW
24 | Number of Heat Pumps | Nos | 4
25 | Testing of Heat Pump |  | The Heat Pump shall be tested at suppliers factory and the same shall be inspected by Consultant/Client.The Heat Pump shall be Certified for Energy Efficiency Rating from any Third Party. Certification copy to be submitted. Make in India Heat Pumps shall be preferred.
B | Storage Tank
1 | Tank Capacity | Liter | 3000
2 | Dimension of Tank - Diameter | mm | Please Specify
3 | Dimension of Tank - Length | mm | Please Specify
4 | Material of Tank - MS - |  | MS - Internally Zinc Thermal Speryed. 5 years Warrantee shall be given for Tank
5 | Tank Dish thickness | mm | 8
6 | Tank Shell thickness | mm | 6
7 | Type of Coating |  | Internal - Zinc Thermal Sprayed and External - Primer with 2 coat's of Red Oxide Paint
8 | Working Pressure | kg/cm2 | 5
9 | Testing Pressure | kg/cm2 | 8
10 | Insulation Type |  | 25 mm thick Polyolefin based per cladded insul tion sheets, etc. completed.
11 | No of Tanks | Nos | 4
C | PIPING
| The complete Scope of piping would include all the piping with fittings, valves, instruments with insulatioin and supports and equipments required for generating and distribution of Hot water Generated from the Heat Pumps upto the supply and return valves as shown in the attached flow diagrams. | Lot
Detail SLD to be submitted & approved by the Consultant before excecution.
D | Room Return Pumping System
1 | Flow - @ 4000 - 5000 LPH @ 12-15 H Head. |  | Specify
(1 W + 1 S By, with Temperature & Timer Automation.)

## Flow diagram with scope
Schematic Flow Distribution Diagram