## BOQ
| BOQ FOR BUSBAR TRUNKING SYSTEM | [6 empty] | VIDYUTSALLAGAR PVT. LTD.
ELECTRICAL CONSULTANT AND ENGINEER
SAVITRI, 113, VINAYAK SOCIETY, SAHAKAR NAGAR NO. 1, PUNE 9.
Email: vidyutsallagar@gmail.com
PHONE 020-24224534
DATE :-09-05-2022
BOQ :- Bus Bar Tunking for 600A and 160 A BBT
CLIENT :- M/s Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit.
0
SR.NO. | PARTICULARS | QTY | UNIT | MATERIAL RATE | MATERIAL AMOUNT | ERECTION RATE | ERECTION AMOUNT | TOTAL AMOUNT
BUSBAR TRUNKING /BUSDUCT
A | 600 A SANDWICH INSULATED BBT
A1 | Supply installation testing and commissioning of 600 A SANDWICH INSULATED TYPE BUSBAR TRUNKING SYSTEM with following specifications & Required all necesory supports. | 40 | MTR. |  | 0 |  | 0 | 0
THE SPECIFICATIONS FOR THE BBT ARE AS FOLLOWS.
BUS BAR TRUNKING:- IP 54
SHORT CIRCUIT RATING :- 36 KA min
SYSTEM VOLTAGE:- 1000V
IEC :- 61439-2
CONDUCTOR :- ALUMINIUM
FIRE RETARDENT PROTECTION CONFIRMING :- IEC 3331/332, NFPA 70
EARTH BUS (EXTERNAL) :- 100%
HOUSING
GALVANISED STEEL SHEET.
THICKNESS:- 2 MM
INSULATION :- CLASS "B''.
INSULATION MATERIAL :- MYLAR
SINGLE BOLT BRIDGE TYPE JOINTS.
ALL HARDWARE IN STAINLESS STEEL WITH HIGHT TENSILE STRENGTH.
BUS BAR SHALL BE TESTED FOR 2.5 KV
VERTICAL SPRING SUPPORT
VERTICAL RIGID SUPPORTS
A1 | Straight Length 3 Mtrs With 3 + 3 outlets for tap off
A2 | End Cover | 1 | Nos |  | 0 |  | 0 | 0
A3 | BUS BAR supports at 2 Meter FOR VERTICAL ORIENTATION OF BBT, as required | 20 | Nos |  | 0 |  | 0 | 0
A4 | End Feed Unit with 600A 4P TM MCCB 36kA(min) and WITH CABLE TERMINATION ARRANGEMENT | 1 | Nos |  | 0 |  | 0 | 0
A5 | Supply installation testing and commissioning of 32 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs.SUITABLE FOR 600 A BBT | 2 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
A6 | Supply installation testing and commissioning of 63 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs. SUITABLE FOR 600 A BBT | 6 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
A7 | Supply installation testing and commissioning of 100 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs. SUITABLE FOR 600 A BBT | 2 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
A8 | Supply installation testing and commissioning of 200 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs. SUITABLE FOR 600 A BBT | 1 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
B | 160 A AIR INSULATED BBT
B1 | Supply installation testing and commissioning of 160 A AIR INSULATED TYPE BUSBAR TRUNKING SYSTEM with following specifications & Required all necesory supports. | 40 | MTR. |  | 0 |  | 0 | 0
THE SPECIFICATIONS FOR THE BBT ARE AS FOLLOWS.
BUS BAR TRUNKING:- IP 54
SHORT CIRCUIT RATING :- 36 KA min
SYSTEM VOLTAGE:- 1000V
IEC :- 61439-2
CONDUCTOR :- ALUMINIUM
FIRE RETARDENT PROTECTION CONFIRMING :- IEC 3331/332, NFPA 70
EARTH BUS (EXTERNAL) :- 100%
HOUSING
GALVANISED STEEL SHEET.
THICKNESS:- 2 MM
INSULATION :- CLASS "B''.
INSULATION MATERIAL :- MYLAR
SINGLE BOLT BRIDGE TYPE JOINTS.
ALL HARDWARE IN STAINLESS STEEL WITH HIGHT TENSILE STRENGTH.
BUS BAR SHALL BE TESTED FOR 2.5 KV
VERTICAL SPRING SUPPORT
VERTICAL RIGID SUPPORTS
B2 | Straight Length 3 Mtrs With 3 + 3 outlets for tap off
B3 | End Cover | 1 | Nos |  | 0 |  | 0 | 0
B4 | BUS BAR supports at 2 Meter FOR VERTICAL ORIENTATION OF BBT | 20 | Nos |  | 0 |  | 0 | 0
B5 | End Feed Unit with 160A 4P TM MCCB 25kA(min) and WITH CABLE TERMINATION ARRANGEMENT | 1 | Nos |  | 0 |  | 0 | 0
B6 | Supply installation testing and commissioning of 32 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs.SUITABLE FOR 160 A BBT | 9 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
B7 | Supply installation testing and commissioning of 63 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs.SUITABLE FOR 160 A BBT | 2 | Nos. |  | 0 |  | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
| TOTAL AMOUNT OF WORK |  |  |  | 0 |  | 0 | 0
| GST 18% | [6 empty] | 0
| TOTAL PROJECT COST INCLUSIVE TAXES | [6 empty] | 0