# TENDER DOCUMENT FOR LIGHT FITTINGS

# FOR

Shri Markendey Solapur Sahakari Rugnalaya

& Research Center Niyamit.

PROJECT: - Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

ARCHITECTS

ARCHITECTS UNITED. 
111/9, ERANDAWANE, 14TH LANE PRABHAT ROAD
PUNE - 411004

- VIDYUTSALLAGAR PVT LTD

- Electrical Consultant& Engineers

- Savitri, 113, Vinayak Society, Sahakar Nagar No. 1, Pune 9.

- vidyutsallagar.anup@gmail.com;

020-24224534, 9372465729

LED LIGHT FITTINGS

- SCOPE: -

- Vendor should provide his proposal along with IES file of light fittings suggested.

- The equipment offered shall be complete with all parts necessary for effective and trouble-free operation. Such parts will be deemed to be within the scope of the supply irrespective of whether they are specifically indicated in the commercial order or not.

- It is not the intent to specify herein complete details of design and construction. The Equipment offered shall conform to the relevant standards and be of high quality, sturdy, robust and of good design and workmanship complete in all respects and capable to Perform continuous and satisfactory operations in the actual service conditions at site and shall have 50000  burning hours life in service.

- Transportation of light fitting at Employer’s store at site should be part of scope.

- Arranging to repair and/or re-order all damaged and short supply items.

- Packing of the Equipments suitable for (all) weather conditions for proper protection.

- Final check-up, testing and commissioning in presence of Employer’s representative.

- All fittings should have warrantee of Five years & warrantee cards of all the fittings duly filled with stamp are to be submitted along with Final bill.

- MAKES OF LED

- PHILIPS- LUMILED

- OSRAM

- NICHIA

- CREE

- SAMSUNG KOREA

- LUMINARY WILL BE PROVIDED WITH FOLLOWING PROTECTION

- Output over voltage & under voltage Protection

- Over temperature

- Output over current and short circuit Auto Recovery

- Input high voltage cut off Auto Recovery

- TEST REPORTS TO BE SUBMITTED BY VENDOR

The product being offered by the vendor should meet our technical parameters. This would be ascertained through the technical information provided by the vendor. The equipment offered should have following certifications and valid as on the due date of the tender, for critical technical specifications and compliance to standards. The minimum certifications required are:-

- Type test certificates

- Acceptance test certificates

- Lumen Depreciation Curve of LEDs used as per L70

- Test report as per LM79 by vendor

- LM 80 report for the LEDs used from manufacturer

- Test report for IS /CE, RoHS & UL certified.

- IP-65 certification report

Vendor shall submit proof of procurement of LEDs and LM-80 test reports of specific LED LM-80 used in the luminary (no other Chip details to 16105 are offered)

TECHNICAL PARAMETERS TO BE CONSIDERED BY VENDOR

| SR. NO. | DESCRIPTION | PARAMETERS TO BE CONSIDERED | ACCEPTED BY VENDOR (YES / NO) |
| --- | --- | --- | --- |
| 1 | AMBIENT TEMPERATURE | 40°C |  |
| 2 | IP RATING OF INDOOR LIGHT FITTING | IP 65 AND ABOVE |  |
| 3 | SURGE PROTECTION | 2 KV AND ABOVE |  |
| 4 | COLOR TEMPERATURE | 5500 - 6500 K |  |
| 5 | STARTING OF LED | INSTANT ON |  |

- IES file of light fittings suggested.

TECHNICAL PARAMETERS TO BE SUBMITTED BY VENDOR

| SR. NO. | DESCRIPTION | VENDORS TO SUBMIT |
| --- | --- | --- |
| 1 | POWER CONSUMPTION OF TOTAL SYSTEM IN WATT |  |
| 2 | LUMEN OUTPUT OF LED FITTING |  |
| 3 | DRIVER WATTAGE |  |
| 4 | WATTAGE OF LED USED |  |
| 5 | SYSTEM EFFICIENCY |  |
| 6 | LED EFFICIENCY |  |
| 7 | AMOUNT OF HEAT DISSIPATED FROM LIGHT FITTING IN WATT |  |
| 8 | LED DRIVER EFFICIENCY |  |
| 9 | POWER FACTOR |  |
| 10 | TOTAL HARMONIC DISTORTION (THD) |  |
| 11 | COLOUR TEMPERATURE |  |
| 12 | COLOUR RENDERING INDEX (CRI) |  |
| 13 | MAKE OF LED USED |  |
| 14 | MATERIAL OF HOUSING/ BODY |  |
| 15 | IP RATING |  |
| 16 | SURGE PROTECTION IN KV |  |
| 17 | IK RATING |  |
| 18 | BEAM ANGLE |  |