## Sheet1
VIDYUTSALLAGAR PVT. LTD.
ELECTRICAL CONSULTANT AND ENGINEER
SAVITRI, 113, VINAYAK SOCIETY, SAHAKAR NAGAR NO. 1, PUNE 9.
Email: vidyutsallagar@gmail.com
PHONE 020-24224534
| BOQ:- MAIN LT PANEL AND LIFT PANEL | [6 empty] | DATE :-09-05-2022
PROJECT :-M/s Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit.
0
SR.NO. | PARTICULARS | QTY | UNIT | MATERIAL RATE | MATERIAL AMOUNT | ERECTION RATE | ERECTION AMOUNT | TOTAL AMOUNT
A | POWER DISTRIBUTION PANEL
Unloading, Installation, testing & commsioning of Following Panels. Panels shall be fabricated out of 16/14 swg CRCA sheet steel, with necessory structural supports in form of structural steel sections. Panels shall be floor mounted.The panel shall be compartmental type with suitable size of bus bar and separate cable and busbarchambers. The cable chambers shall be free from any live open connections. Multifuction meters for all incoming feeders, Indication lamps for all incoming and outgoing feeders for phase identifications and for indication of Switch status. (All panels shall comply to IEC 61439-1-2.)
1 | 630 KVA SOURCE SELECTION | 1 | NOS. |  | 0 |  | 0 | 0
PLEASE REFER SLD FOR MORE CLARIFICATIONS
PANEL SHALL BE INDOOR TYPE- IP-43
FORM 3B
ALUMINIUM BUS
FAULT CURRENT :- 40 KA
All panels switchgear will be provided with lockout tagout (loto)arrangement. Indications positions for all incomers phase indication with switch position. For all outgoings for switch on off & trip indication. All ACBs with - phase indication with switch position. Protections: Surge protection on Incomer.Single phasing preventer on incoming bus for phase in balance and single phase preventions. Panel shall consist of Auto Changeover Logic. All incomers meter shall be :- Schneider :- EM- 2230 series or equivalent. All outgoing meter shall be :- Schneider :- EM- 6400 NG series or equivalent. All meters shall be communication capable
INCOMING
SYNC PANEL OUTPUT 2 OUTGOING 1000 A FP EDO ACB 40 kA µP LSIGN
630 KVA TRANSFORMER OUTGOING 1000 A FP EDO ACB 40 kA µP LSIGN
OUT GOING
HVAC TERRACE PANEL OUTGOING 1000 A TP EDO ACB 40 kA µP LSI
2 | 1000 KVA SOURCE SELECTION | 1 | NOS. |  | 0 |  | 0 | 0
PLEASE REFER SLD FOR MORE CLARIFICATIONS
PANEL SHALL BE INDOOR TYPE- IP-43,FORM 3B,
ALUMINIUM BUS
FAULT CURRENT :- 40 KA
All panels switchgear will be provided with lockout tagout (loto)arrangement. Indications positions for all incomers phase indication with switch position. For all outgoings for switch on off & trip indication. All ACBs with - phase indication with switch position. Protections: Surge protection on Incomer.Single phasing preventer on incoming bus for phase in balance and single phase preventions. Panel shall consist of Auto Changeover Logic. All incomers meter shall be :- Schneider :- EM- 2230 series or equivalent. All outgoing meter shall be :- Schneider :- EM- 6400 NG series or equivalent. All meters shall be communication capable
INCOMING
SYNC PANEL OUTPUT 3 OUTGOING 1600 A FP EDO ACB 40 kA µP LSIGN
1000 KVA TRANSFORMER OUTGOING 1600 A FP EDO ACB 40 kA µP LSIGN
OUT GOING
NEW BLDG MDB OUTGOING 1600 A TP EDO ACB 40 kA µp LSI
OLD BLDG MDB OUTGOING 800 A TP EDO ACB 40 kA µP LSI
3 | NEW BLDG MDB | 1 | NOS. |  | 0 |  | 0 | 0
PLEASE REFER SLD FOR MORE CLARIFICATIONS
PANEL SHALL BE INDOOR TYPE- IP-43
FORM 3B
ALUMINIUM BUS
FAULT CURRENT :- 40 KA
All panels switchgear will be provided with lockout tagout (loto)arrangement. Indications positions for all incomers phase indication with switch position. For all outgoings for switch on off & trip indication. All ACBs with - phase indication with switch position. Protections: Surge protection on Incomer.Single phasing preventer on incoming bus for phase in balance and single phase preventions. Panel shall consist of Auto Changeover Logic. All incomers meter shall be :- Schneider :- EM- 2230 series or equivalent. All outgoing meter shall be :- Schneider :- EM- 6400 NG series or equivalent. All meters shall be communication capable
INCOMING
NEW BLDG MDB OUTGOING 0
RTPFC PANEL-340 KVAR OUTGOING 630 A TP MCCB 40 kA µP LSI
OUT GOING
FIRE FIGHTING PANEL OUTGOING 160 A TP MCCB 40 kA µP LSI
PLUMBING LOADS+HEAT PUMP OUTGOING 160 A TP MCCB 40 kA µP LSI
LIFT DB OUTGOING 160 A TP MCCB 40 kA µP LSI
BBT NCR OUTGOING 800 A TP EDO ACB 40 kA µP LSI
BBT CR OUTGOING 315 A TP MCCB 40 kA µP LSI
OLD BUILDING MAIN PANEL OUTGOING 500 A TP MCCB 40 kA TMD LSI
X-RAY OUTGOING 100 A TP MCCB 40 kA µP LSI
CT SCAN OUTGOING 125 A TP MCCB 40 kA µP LSI
MRI OUTGOING 200 A TP MCCB 40 kA µP LSI
COMPRESSOR OUTGOING 100 A TP MCCB 40 kA µP LSI
SUCTION MACHINE OUTGOING 40 A TP MCCB 40 kA µP LSI
PHYSIOTHERAPY OUTGOING 32 A TP MCCB 40 kA µP LSI
INFORMATIVE GLOW SIGN OUTGOING 16 A TP MCCB 40 kA µP LSI
MEDICAL GASSES OUTGOING 32 A TP MCCB 40 kA µP LSI
DIALYSIS OUTGOING 40 A TP MCCB 40 kA µP LSI
CSSD OUTGOING 125 A TP MCCB 40 kA µP LSI
LAMINAR FLOW OUTGOING 32 A TP MCCB 40 kA µP LSI
ULTRAVIOLET LIGHTS OUTGOING 16 A TP MCCB 40 kA µP LSI
SPARE OUTGOING 1000 A TP EDO ACB 36 kA µP LSI
SPARE OUTGOING 630 A TP MCCB 36 kA µP LSI
SPARE OUTGOING 160 A TP MCCB 36 kA µP LSI
SPARE OUTGOING 63 A TP MCCB 36 kA µP LSI
4 | LIFT PANEL | 1 | NOS. |  | 0 |  | 0 | 0
PLEASE REFER SLD FOR MORE CLARIFICATIONS
PANEL SHALL BE INDOOR TYPE- IP-43
FORM 3B
ALUMINIUM BUS
FAULT CURRENT -10 kA
All panels switchgear will be provided with lockout tagout (loto)arrangement. Indications positions for all incomers phase indication with switch position. For all outgoings for switch on off & trip indication. All ACBs with - phase indication with switch position. Protections: Surge protection on Incomer.Single phasing preventer on incoming bus for phase in balance and single phase preventions. Panel shall consist of Auto Changeover Logic. All incomers meter shall be :- Schneider :- EM- 2230 series or equivalent. All outgoing meter shall be :- Schneider :- EM- 6400 NG series or equivalent. All meters shall be communication capable
INCOMER
LIFT DB INPUT 160 A TP MCCB 10 kA TMD LSIGN
OUT GOING
LIFT 1 (3 ph) INPUT 32 A FP RCBO 30 mA rated 10 kA TMD LSI
LIFT 1 (1ph) INPUT 6 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 2 (3 ph) INPUT 32 A FP RCBO 30 mA rated 10 kA TMD LSI
LIFT 2 (1ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 3 (3 ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 3 (1ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 4 (3 ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 4 (1ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 5 (3 ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
LIFT 5 (1ph) INPUT 32 A DP RCBO 30 mA rated 10 kA TMD LSI
| TOTAL |  |  |  | 0 |  | 0 | 0
| GST 18% | [6 empty] | 0
| TOTAL PROJECT COST INCLUSIVE TAXES | [6 empty] | 0