TENDER DOCUMENT

SUPPLY, TESTING & COMMSIONING OF

LT PANELS

CLIENT: -M/s Shri Markendey Solapur Sahakari Rugnalaya

& Research Center Niyamit.

PROJECT: - Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

ELECTRICAL CONSULTANT

- VIDYUTSALLAGAR PVT LTD

- Electrical Consultant& Engineers

- Savitri, 113, Vinayak Society, Sahakar Nagar No. 1, Pune 9

- vidyutsallagar.anup@gmail.com.

- 020-24224534, 9372465729

ENQUIRY FOR SUPPLY OF LT PANEL & POWER FACTOR CORRECTION PANELS

From:          __________________________________
__________________________________ 
__________________________________ 
__________________________________

Date:

To,

M/s Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

Kind Attn.

Mr.

Dear Sir,

Sub: - Supply of LT PANEL for M/S Solapur Sahakari Rugnalaya Niyamit, Solapur Maharashtra.

We have pleasure in submitting herewith Tender Quotation for the above mentioned works, duly completed in all respects.

- We represent that we have the adequate experience and expertise in handling and delivering the Work as envisaged in the Enquiry as above in accordance with the quality and time period desired by you.

- We have read and studied the entire Enquiry Document for the proposed work we agree to abide by them.

- We agree to execute and complete the proposed work at the rates quoted herewith.

- We have inspected the site of works and acquainted ourselves with the local conditions. We will not claim any extra amounts for reasons arising out of site conditions. Rates quoted by us include all such eventualities.

- The rates quoted in the Enquiry shall be valid for three months from the date of opening of the Enquiry.

- The bid document shall be filled properly and all relevant information asked for shall be provided in due format.

- Bidders are requested to give deviations/comments/assumptions/alternatives clearly in deviation pages / separate pages based on their observations.

- Base BOQ shall not be altered. Deviations for technical specifications shall also be clearly given in the bids. Technical specifications for which deviations are not provided with the bids or not accepted during negotiations shall not be revised after order.

- I/we understand that you are not bound to accept the lowest or any tender you may receive. This Tender document shall be a part of the Contract.

I/ we do hereby offer to execute the work under the Item rate Contract at the respective rates mentioned in the Schedule of Quantities. Cost of this works out to

Rs…………………………………..……………………./-

(Rs.……………………………………………………………………………………………………………….………………………………………………………….Only)

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)

TENDER DETAILS

- Sealed item rate tenders are invited on behalf of M/S- Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit, for Supply, testing and commissioning of LT Panels & Power factor correction panels, as per BOQ.

- The purchaser reserves the right to accept any tenders received after the expiry of the time notified.

- No hard copy should be submitted to office. Only soft copy is required

- Last date of tender submission is dd/mm/yyyy on or before 1200 Hrs.

- The entire delivery of material is to be completed within __ weeks from the date of letter of intent or work order

- The Owners at their sole discretion can accept any Tender or reject all the received Tenders. This note shall form part of the Contract.

- The Tender is an item rate Tender, though the total value of Contract shall appear on the letter of intent or work order, the successful Contractor shall be paid as per measured, erected and certified quantities of ‘Bill of Quantities’ on pro rata basis as per the payment terms.

- Submission of queries related to bid – on dated 31/05/22,   19:00 Hrs.

Please note: - queries raised after dated 30/05/22,   19:00 Hrs. will not be entertained.

- Please submit your queries on following Email-ids.

vidyutsallagar.anup@gmail.com

In case, any clarification is required, the Bidders shall obtain the same from the Consultant/Client in writing. All such clarifications shall be binding both on the Purchaser/Consultant and the Bidder.

At any time prior to the deadline for submission of Bids, the Purchaser/Consultant may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, modify the tender document by amendments.

The prices & rates quoted by the Bidder’s shall be valid & shall be kept open for acceptance for a minimum period of thirty(30) days from the date of opening of tender.

The acceptance/ rejection of the quotation will rest with the purchaser, who does not bind himself to accept the lowest quotation or any quotation & reserves to himself the full rights for the following without assigning any reason whatsoever.

Whenever it is stated in this contract that such and such a supply is to be effected or such and such a work is to be carried out, or provided it shall be understood that the same shall be effected/carried out by the supplier within the contract price, unless a different intention is specifically and expressly stated herein or otherwise explicit from the context.

Project information: -   	Solapur Sahakari Rugnalaya Niyamit

on F.P. No. 19/2, Pachha Peth,

Solapur 413005.

Name of work: - 	Supply, testing and commissioning of LT Panels

Purchaser/ owner: - 	M/S. M/s Shri Markendey Solapur Sahakari

Rugnalaya & Research Center Niyamit

Electrical consultant: -	VIDYUTSALLAGAR PVT LTD

Electrical Consultant & Engineers

Savitri, 113, Vinayak Society,

Sahakar Nagar No. 1, Pune 9.

Contact Person: - Mr.Anup. A. Karandikar

Project Design engineer

Mob: - +91 7875054055

E-mail:- vidyutsallagar.anup@gmail.com

Site conditions: -		Design ambient temperature

Maximum 	45º C

Minimum	14º C

Relative humidity: 50 % RH

Altitude above mean sea level: 457 feet

Installation: Indoor

LT PANELS

Scope include

- ALL THE PANELS MUST BE COMPLYING TO IEC 61439 -1-2.

- THE PANELS SHALL BE INTERNAL ARC CERTIFIED AS PER IEC 61641, ALONG WITH ARC FLASH RELAY FOR PROTECTION.

- This specification covers design, manufacturing, testing commissioning of Supply Installation & commissioning of LT PANELS and Power factor correction panels.

- Completeness of the equipment shall be the responsibility of the supplier. Any equipment, fittings, and accessories which may not be specifically mentioned in the specification or drawings, but which are usual or necessary for the satisfactory functioning of equipment (successful operation and functioning of the equipment being supplier’s responsibility) shall be provided.

- Specifically it is a turnkey contract with sets handed over to direct use.

- All fitting and accessories or apparatus which may have not been specifically mentioned below, which are necessary and essential for the efficient working of the equipment, shall be deemed to be included in the scope.

- Transportation of LT panels at Employer’s store at site should be part of scope.

- Packing of the Equipments suitable for (all) weather conditions for proper protection.

- Supervision of unloading of the LT panels is also to be considered in the scope.

- Arranging to repair and/or re-order all damaged and short supply items.

- Installation of panels at site.

- Supervision from Panel vendor at the time of Final check-up, testing and commissioning in presence of Employer’srepresentative.

- Testing commissioning and handing over to client.

Design, Manufacture, Assemble, Supply, Installation Testing & Commissioning of Sheet steel fabricated panel, The panel shall be design verified as per the standards, The panel and the associated equipment including switchgear, control gear, Busbar supports, Busbar orientation, Busbar links etc shall be identical in construction to the assembly.

Standards

The equipments covered under this specification shall conform to the latest revisions of relevant IndianandInternational Standards some of which are listed below.

- IEC 61439-Low voltage switchgear & control gear assemblies (Assemblies)

  - Part 1: General Rules

  - Part 2: Power switchgear and control gear assemblies

- IS : 694 PVC insulated cables

- IS: 4237 General requirements for switchgear & control gear for voltages not exceeding 1000volts.

- IS : 722 Specification for ac electricity meters

- IS: 1248 Specification for direct acting indicating analogue electrical measuring instruments & itsaccessories.

- IS: 5578 Guide for marking of insulated conductors.

- IS: 12021 Specification for control transformers for switchgear & control gear voltage not exceeding1000V.

- IS: 3231 Specification for electrical relays for power system protection.

- IS: 13703 Low voltage fuses for voltages not exceeding 1000V AC or 1500V DC.

- IS: 2705 Specification for current transformers.

- IS: 3156 Specification for voltage transformers.

- IS: 5578 / IS 11353 Marking and arrangement of bus bars.

- IS : 11353; 1985 Guide for uniform system of moving and identification of conductor &apparatus

- IEC 60529/IS 2147; 1962 Degree of protection provided by enclosure

- IEC 61439; Low voltage switchgear and control gear assemblies

- IEC : 61439; Particular requirement for bus way

- IEC 60947 / IS 13947 Low voltage switchgear & Control gear

- Indian electricity rules – 1956

System particulars:

- Power supply: 415V +or -10%, 3Ph, 4 wire

- Power supply: 380 +or -10%, 3Ph, 4 wire

- Frequency: 50Hz +or - 3%

- Control Voltage: 230V, 50Hz, 1Ph, AC Supply

- Space heater supply: 230V, 50Hz, 1Ph,

- AC Supply Three Phase Symmetrical fault level: 36 KA for 1 sec.

- Grounding : Solid grounded

General Requirement and Selection of Components:

- CONSTRUCTION

- The panel shall be free standing, floor mounting, compartmentalised, cubical type panel with framed structure and bottom channel frame of I S M C 75 x 6 mm thick MS section.

- The frame structure shall be made out of 14 S W G C R C A sheet. All partitions shall be of 16 S W G C R C A sheet.

- The terminals of the switchgear shall be modified to provide ample space fastening of cables and to keep sufficient clearance between leads and lugs of different phases.

- For each cable, Gland plate of 6” x 6” will provide.

- The panel shall be made dust and vermin proof using neoprene gaskets.

    - Sheet Steel –			CRCA

    - Base frame –			I S M C 75 x 6 mm thick MS section

    - Gland Plate –			14 S W G C R C A sheet

    - frame structure–		14 S W G C R C A sheet

    - Mounting Plate –		14 S W G C R C A sheet

    - All partitions –			16 S W G C R C A sheet

    - Front  door - 			16 S W G C R C A sheet

    - Rear door - 			16 S W G C R C A sheet

- CLEARANCES

Operating voltage is 415 V. Hence Minimum clearances are as follows

- Phase to phase		32 mm.

- Phase to neutral 		32 mm.

- Phase to earth		32 mm.

- Neutral to earth		32 mm.

- SUPPORTS

The material used for cable lead supports shall be strong enough to take mechanical load of cable leads.

- CLEANING AND PAINTING

Fabricated sections shall be thoroughly cleaned by 7 tank process which include

  - Alkaline degreasing

  - Cold water rinsing

  - Acid pickling

  - Water rinsing

  - Phosphating

  - Passive

- Sections are then painted with 2 coats of corrosion resistant primer and oven dried under controlled temperature.

- Then 2 coats of Siemens Gray paint are given.

- Thickness of coating 125 microns.

- All parts which are used inside the panels will be of C R C A and Electroplated with coating thickness of 7-15 microns.

- NAME PLATES

- Name plates for each feeder and compartment.

- Lettering on name plate must be readable from 20 feet.

- Red coloured boards in English will be provided on bus bar chamber.

- BUS BARS

- High conductivity aluminium alloy of grade E9 as per IS 5082 shall be used for bus bars.

- Bus bar selection shall be considered after short circuit current density and surface density.

- Bus bar calculation must provide with GA.

- Bus bar supports shall be suitable for fault level of 50 kA.

- Connections shall be done using adequate size of plated hardware with washers and spring washer’s sets.

- The interconnections shall be made with solid bus bars as far as possible.

- Colour coded sleeves shall be used on bus bars.(Red, yellow, blue for phases, black for neutral, green for earth. )

- Where ever necessary flexible copper cables shall be used for interconnection between bus bars and switches. Cutting, shouldering, sudden tapering of bus links will not be permitted. Proper type of lugs shall be used with cables. The cable links shall be adequately supported using binders.

- SHROUDING

- Acrylic shrouding for protection will be provided in switch compartment as well as on normally live parts

- SWITCHES

- All the switches used shall be of approved make.

- All switches shall have door interlocks.

- MEASURING INSTRUMENTS AND INSTRUMENT TRANSFORMERS

- Direct reading instruments shall be in confirmation with IS 1248 and of accuracy class 1.0.

- Voltmeters and ammeters shall be of moving iron type, backed up by, suitable current transformers, potential transformers, MCB’s, selector’s switches etc.

- Current transformers shall be wire wound single pole resin cast class 1.0 accuracy for metering and 5.0 for protection. Separate C T‘s shall be provided for metering and protection.

- The polarities and coil terminals shall be prominently marked and minimum 2.5 sq. mm. Copper multi-strand wires shall be used for interconnection. Terminal shorting arrangement shall be provided for C T‘s.

- INTERNAL WIRING

- Internal wiring for control circuits shall be made with 1100 V grade single or multi-strand copper PVC cable.

- Power wiring shall be done either with copper flexible PVC insulated cable of 1100 V grade or with solid copper conductors.

- The minimum size of control wiring shall be 2.5 sq. mm. Copper for Current circuits and 1.5 sq. mm. Copper for other circuits.

- The wiring shall be terminated at the respective terminal with suitable crimp type lugs.

- There shall not be more than two wires connected to single terminal.

- POWER CABLE TERMINATION

- Adequate volume shall be kept for end termination at every terminal.

- Front doors and gland plates shall be 2 mm. thick. Every cable connected to the panel shall have individual gland plate. The provision shall be made for 25 % extra gland plates to facilitate future alterations. All gland plates shall be interchangeable and hence have standard sizes.

- The recommended size is 6” X 6” folded plate fitted to panel using ¼” nut bolts covering a cut out of 4” X 4” size. The minimum clear distance 750-mm from gland plate to the incomer terminal shall be maintained to facilitate quality termination.

- SURGE ARRESTOR

- On Main Panel Board CLASS B type surge arrestor should be provided. The KA rating should be 36 KA minimum. The panel should be protected against surges up to 0.9 KV.

- On Floor Panels the CLASS B type surge arrestor should be provided. The KA rating should be 36 KA min. The panel should be protected up to 0.9 KV surges.

- SPACE HEATERS

- Each vertical section of the panel shall be provided with thermostat controlled anti -condensation, industrial strip continuous duty type space heaters rated for 240 Volts ±10%,single phase, 50 Hz. The heaters shall be provided with DP MCB.

- Wiring of space heaters in each panel shall be grouped and brought out to easily accessibleterminals for connection to power supply, through MCB.

- Each switchboard shall be provided with plug-socket with MCB for the connection of hand lamprated 240 V, 50 Hz. single Phase.

- DISTRIBUTION BOARDS

- The general specifications will be as above.

- All boards shall have MCB‘s as outgoing feeders.

- The container shall be of the same make as of MCB‘s, unless otherwise specified. The type of the board is specified in the BOQ.

- MCB‘s shall confirm to IS 8828 and shall have 10 kA breaking capacity.

- TESTING AND INSPECTION

- The panel board and ACB shall be of type tested design. Type test certificates of similar panel board and ACB shall be furnished. In the absence of type tested design, the contractor has to type test the panel at his own cost and type test certificates shall be furnished. All routine tests as per IS shall be conducted on the completely assembled panel board. Routine tests shall be witnessed by client’s representative. Witnessing inspection may be waived at client’s discretion. However, witnessing the routine tests will not absolve the contractor of his responsibilities and contractual obligations. Routine test certificates of panel board, ACB, MCCB, SFU, CT, relays, meters shall be furnished by the contractor.

- Pre-delivery testing and inspection shall be offered to the Electrical Consultant/the Company/architect.

- Following tests shall be carried out at manufacturers place and test reports for the same shall be submitted to the architects before inspection.

  - Panel Dimension checking.

  - Visual Inspection (Compartment check )

  - Checking of Bill of material.

  - Mechanical Functioning test.

  - Insulation resistance test at 2.5 kV for 1 min. durations. The insulation resistance shall be 100 m-ohm minimum.

  - High voltage test as per relevant I S.

  - Functional tests.

- VOLTMETER

- Voltmeter shall comply with BS: 90. The dial of the meter shall be square in shape of 96 x 96 mm. or 144 x 144 mm. in size. The voltmeter shall be moving iron type, flush pattern, with dust and moisture proof enclosure.

- The voltmeter selector switch shall be arranged to provide line to line voltage reading and line neutral voltage.

- AMMETER

- Ammeter shall comply with BS: 89. The dial of the ammeter shall be square in 96 x 96 mm. or 144 x 144 mm. in size. The ammeter shall be moving iron type, flush pattern with dust and moisture proof enclosure. The range of the ammeter shall be in accordance with 1 to 1.5 times the feeder full load current. Separate current transformer shall be provided for all ammeters.

- CURRENT TRANSFORMER

- When required C.T.s shall be provided for current measuring. Each phase shall be provided with separate current transformer of accuracy Class I and suitable VA burden for operation of associated metering and controls. Current transformer shall be in accordance with IS: 2705 - 1964 as amended up to date.

- PUSH BUTTONS

- The push button unit shall comprise of the contact element, a fixing holder, and a push button actuator. The push button shall be momentary contact type. The contacts shall be of silver alloy and rated at 10 Amps. Continuous current rating. The actuator shall of standard type and colour as per its usage for ON, OFF and TRIP.

- INDICATING LAMPS:

- Indicating lamps shall be transformer operated low voltage rated and shall be supplied complete with translucent covers to diffuse the lamp light.

- Colour shade for the indicating lamps shall be as below :

  - ON indicating lamp		:	Red

  - OFF indicating lamp		:	Green

  - TRIP indicating lamp		:	Amber

  - PHASE indicating lamp 		:	Red, Yellow, Blue

- The panel shall be provided with lifting hooks / eye bolts for handling.

- Any other part / accessories not specifically mentioned above but considered necessary for safe and reliable operation.

- EARTHING

- Aluminium earthing bus shall be provided for the entire length of the panel and shall be rated tocarry maximum fault current.

- Earth bus bar shall be located at the bottom/top of the panel.

- Allmetallic non-current carrying parts of the switchgear shall be bonded together and connected to the switchgear earth busbar.

- All doors shall be bonded to the main structure by means of a flexible copper connectionArranged so that it cannot be trapped as the door is opened or closed.

- With-drawable parts (e.g. circuit breakers) shall be effectively earthed until they are completelywithdrawn with all power and control connections disconnected.

- Provision shall be made, for earthing cable screen and armouring to the earth bus bar, near thegland.

- Provision shall be made for connection from earth bus bar to the main earthing bus bar comingfrom the earth pit on both side of the panel.

- Earth bus bar shall be rated to carry the rated symmetrical short circuit current of associated panel for one second and earth bus bar shall be supported to withstand stresses induced by themomentary current of value equal to the momentary rating of the associated Panels.

- Vendor has to submit earth bus calculation along with GA Drawing at the time of drawingapproval.

- Each earthing point shall be marked with letter ‘E’.

- DRAWINGS AND DOCUMENTS

- Following drawings shall be furnished by the contractor for approval of Engineer-in-Charge.

  - Data sheet as per format enclosed in the tender document

  - General Arrangement drawing showing plan with gland plate details, elevation and side view sections

  - Sectional elevation showing bus bar arrangements

  - Incoming bus duct joint flange and bus bar details

  - Single Line Diagram of LT panel board

  - Control Scheme Diagram

  - Wiring Diagram

  - Terminal Block details

  - Bus bar sizing calculation

  - Labels shall be anodised aluminium with white engraving on black back ground. They shall be properly secured with fasteners or PVC with white engraving on black back ground.

Air Circuit Breaker:

ACBs shall be tested as per IEC 60947-2. All Incoming ACBs shall be EDO Type as indicated in the SLD. ACBs shall be rated for 50degrees ambient temperature. No derating of breaker is allowed.

All Outgoing Air Circuit Breakers shall be of Electrical Draw-Out Type. ACBs shall have integral LSING Protection through Micro Processor based Release with display showing current parameters. The release shall be self powered, and if required separate power supply shall be provided.

ACBs must be provided with Rogowski type CTs throughout the range of ACBs. These CTs should not

Saturate on higher currents. For 4 pole ACBs, neutral CT shall be integral. For 3 pole ACBs, neutral protection shall be provided with external neutral CT of OEM. 4th pole of the ACB shall be 100%. Half size of phase for neutral will not be acceptable.

Breaker release must have I2 t characteristics in addition to standard characteristics to achieve discrimination with numerical relay of medium voltage switchgear. ACB shall have ready to close interlock for safe operation of breaker. ACB shall have minimum 2NO+2NC auxiliary contacts.

Earth fault protection provided by release should be in absolute values in order to achieve minimum setting of earth fault.

Moulded Case Circuit Breaker-

MCCBs shall be fixed type, 4 poles/ 3 poles as mentioned in SLD for incoming and outgoing feeders.

MCCBs shall have double rotary mechanism as default feature for lesser tripping time in the event of fault.

MCCBs up to 630 A shall be Microprocessor /thermal magnetic with adjustable thermal and adjustable magnetic release as per BOQ, SLD.

MCCBs shall preferably have colour coded accessories for easy identification and inventory maintenance.

OEM shall provide selectivity study with its own power distribution software for release setting.

Earthing:

Earthing - Two earth terminals shall be provided on each side of switchboard. An earth bar size must

Aluminium suitable for kA rating mentioned in BOQ, SLD for 1 sec. shall be provided. The earth bar shall be electrically continuous and shall run the full extent of each board. This earth bar shall be on the same side as the cable entry. Each unit shall be constructed to ensure satisfactory electrical continuity between all metal parts not intended to be alive and earth terminals of the unit. Suitable holes with bolts and nuts shall be provided at each end of earth bar of switchgear for connection to a main Earthing grid. The earth bar shall be accessible in each cable entering compartment either directly or through a branch extension to ground the cable armour and shields. 10 mm Ø holes shall be drilled and hardware for connection provided through the earth bus.

Internal Wiring:

Minimum size of conductor for power circuits shall be 2.5 sq. mm copper or 6 sq. mm aluminium. All control wiring except CT secondary wiring shall be carried out with minimum 1.0 sq. mm copper conductor. CT secondary wiring shall be carried out with 1.5 / 2.0 sq. mm copper conductor.

All wiring shall be securely fixed and neatly arranged to enable easy tracing of wires. All terminal blocks and wires shall be tagged for identification in accordance with IS 11353. All wiring for external connections shall be brought out to the individual terminals on a readily accessible Terminal block;

All terminal block shall be shrouded or provided with transparent covers. Clamp type control terminal blocks shall be provided for outgoing control cables. Minimum 10% spare Terminals shall be provided for future use. Control terminal block shall be separated from power terminal blocks by means of an insulating barrier.

Cable Terminations and Marshalling Box:

Cable entry to switchgear as mentioned in the BOQ. Ample space shall be provided in the cable compartment to accommodate XLPE insulated aluminium conductor cable as specified in the technical particulars. Removable undrilled gland plate shall be provided for termination of Cables.

Cleaning and painting:

Fabricated sections shall be thoroughly cleaned by 7 tank process which include

- Alkaline degreasing

- Cold water rinsing

- Acid pickling

- Water rinsing

- Phosphating

- Passive

- Sections are then painted with 2 coats of corrosion resistant primer and oven dried under controlled temperature.

- Then 2 coats of polyurethane based Siemens Gray paint shall provide

- Thickness of coating 135 microns.

- All parts which are used inside the panels will be of C R C A and Electroplated with coating thickness of 7-15 microns.

Name Plates & Label

One name-plate giving designation of the switchboard shall be affixed prominently on top. Details of Designation shall be specified. Labels giving following details shall be affixed on each feeder panel:-

- Feeder No - As per feeder list

- Equipment tag Number and Description

- Rating (KW/KVA/AMP)

All components whether mounted inside the switchboard or on the door shall be permanently and clearly labelled with reference number and/or letter of their function.

Labels for feeder panel designation shall be fixed on the front side of respective panels with Special rivet made of nylon. These labels shall be identical size to permit interchange.

Lettering on name plate must be readable from 20 feet.

Testing and Inspection

The following tests shall be carried out at manufacturer's works and witnessed by Buyer:

Vendor shall demonstrate their capability and conformance to the IEC 61439 with all the type test reports comprising of the SCPD & Aluminium bus-bars for all the ratings specified in the SLD / enquiry.

- Operation of all meters.

- Secondary wiring continuity test with a low voltage (6 volts) tester.

- Insulation test with 1000 volts megger, before and after H. V. test.

- H. V. test at 2.5 kV for 1 minute.

- Earth continuity test with a low voltage (6 volts) tester.

- Simulating control circuits for various operations of feeders

- C. T. Polarity Test.

SWITCHGEAR DIMENSIONAL LIMITATIONS

The overall height of the switchgear shall be limited to 2400 mm for all types of panels.

Panel should have integral base frame of 75mm, hence total panel height should not be more than 2475mm.

The height of the operating handle, push buttons etc. shall be restricted between 300 mm and 2000 mm from finished floor level.

Other dimensional limits if any will be specified by client specified separately.

DRAWINGS AND DOCUMENTS

Following drawings shall be furnished by the contractor for approval of Engineer-in-Charge.

- Technical Data sheets for switchgears

- General Arrangement drawing showing plan with gland plate details, elevation and side view sections

- Internal GA drawings showing busbars, busbar supports, switchgears, control equipments etc.

- Bus bar sizes used for phases, neutral and earth, with temperature rise calculation

- Number of nut bolts and their sizes used.

- Type of washers and their numbers at each joint

- Sectional elevation showing bus bar arrangements

- Incoming bus duct joint flange and bus bar details

- Single Line Diagram of LT panel board

- Control Scheme Diagram

- Wiring Diagram

- Terminal Block details

- Bus bar sizing calculation

- Labels shall be anodised aluminium with white engraving on black back ground. They shall be properly secured with fasteners or PVC with white engraving on black back ground.

- Bill of Material including type of gaskets, air filters, fans, locks, hinges, and such other materials. This is in addition to switchgear, instrumentation and control gears used.

Delivery and commissioning of panels

- Panel vendor engineer shall be present at site for supervision of unloading procedure at site.

- Panel vendor engineer shall be present at site to supervise the assembly of panels at site, when panels will be delivered in sections.

- It’s a Panel vendor responsibility of checking proper tightness of all the nut-bolts and provides the pre-commissioning report at the time of energizing the panels.

- Panel vendor technicians will take care of assembly and nut bolt tightening work, along with pre-commissioning check. All the labour work, including allied expenses, has been included in our panel cost.

- Panel vendor engineer shall be present for commissioning of all the panels.

- Panel vendor shall provide training on operation and maintenance of panels, to Electrical maintenance staff of client.

Handing over

- The set of final handing over of documents will include

- All certifications related to IEC 61439 compliance, including the mention of the same on name plate, names of certificate holder, actual assembler and OEM.

- All routine test reports carried out on panels.

- As built drawings for each panel.

- Guarantees and warrantees of switch gears, instrumentation and control gears along with operation and maintenance manuals.

After sale service

- The response time for any type of query shall be 24 hours maximum.

- Panel vendor shall provide contact details of persons and parties, who will support in case of any need, regarding these panels.

POWER FACTOR CORRECTION PANELS (RTPFC UNIT)

- This specification covers design, Manufacture, supply, installation, testing, commissioning of Thyristor based real time Power factor control unit (RTPFC unit) with capacitor banks suitable for continuous duty.

- RTPFC relay will be Beluk or equivalent make & the type of capacitors shall be All Polypropylene type double layer conforming to IS 13925, PI, 1997.

- The design, manufacture and performances of the power factor correction panel with capacitor banks shall comply with all currently applicable statutes, regulations and safety codes in the locality where it will be installed. The equipment will also conform to the latest applicable Indian / British / IEC standards. In particular the equipment shall confirm latest revisions of the following.

  - IS: 12672 		Capacitors for power system.

  - IS: 13340 & 13341   	Capacitor marking

  - IS:  2208		HRC cartridge fuses and links up to 600 Volts.

- When the above standards are in conflict with the stipulation of this specification, this specification supersedes them.

- Capacitor bank shall comprise of identical three units of Single Phase capacitors. The individual capacitor unit shall be manufactured out of APP design, comprising of bi-axially oriented metallised polypropylene film. The capacitor shall consist of many such elements in series / parallel combinations for getting desired KVAR output. The dielectric losses of capacitor shall be restricted to 0.5 watts per KVAR. The phase terminal connections of the capacitor unit shall be brought out at the top, for suitable connections. The capacitor shall be provided with suitably rated discharge resistor. The capacitor shall be provided with over pressure interrupter mechanism, which will automatically disconnect faulty capacitor unit from the network without bursting, bulging or exploding the capacitor.

- The capacitor control panel shall be Automatic as specified in the data sheet and bill of quantity. The panel for capacitor shall be fabricated from 2 mm thick sheet steel and shall be finished with 7 tank process followed by powder coating. Earthing terminal shall be provided and also the panel shall be provided with suitably rated T. P. copper bus bar supported on epoxy insulator.

- Each capacitor unit shall be connected to main bus bar through contactor of suitable rating with safety margin.  Protective HRC fuses of suitable rating shall be provided with base / holder as mentioned in the drawing. Connection shall be made with PVC   insulated flexible copper cables having crimped copper lugs.

- All capacitor units shall be earthed, sufficient ventilation shall be provided to limit the temperature rise to 85oC. Cooling fans shall be provided to each heat sink as per requirement. Drawing pocket shall be provided for each panel at the door.

- Also a 15 Amp switch socket and the lamp holder shall be provided for panel illumination at suitable location.

- The main Bus bar shall be terminated on suitably rated ACB/MCCB. Detachable gland plates shall be provided with suitable knockouts for incoming cable connection from bottom / Top as specified. Capacitor unit shall be mounted on rigidly constructed frame. The panel shall be mounted on MS stand for easy installation.

- The panel shall be provided with lifting hooks / eye bolts for handling.

- Automatic Power Factor Correction Relay shall be provided with all related circuits and three loads CT’s for each phase in order to control achieve target Power Factor OR unity as per setting.

- The controller shall be able to correct Power Factor within 40 to 60 m sec.

- The panel shall be provided as per respective drawing.

- The capacitor shall be switched ON and OFF using Thyristor controlled from RTPFC relay.

- Average compensation required and compensation supplied shall be continuously monitored for all the three phase simultaneously and total low KVAR requirement shall be calculated accordingly. It should automatically switch ON and OFF the capacitor bank so as to mention the set target power factor. The power factor should be corrected in 40 to 60 m. sec.

- Forced cooling system for RTPFC bank shall be provided.

- Diagnostic capability shall be provided for analyze and indicate type of error coding system.

- Power factor controlling shall be done on entire cycle. Proportionate correction or cutting A.C. waveform will not be allowed.

- The controller shall be capable to work at phase to phase voltage between 200 to 440 volts.

- Digital controller shall be provided with  minimum indication of line voltage and current, capacitor current, Power factor, active power / reactive power/ apparent power, injected capacitive KVAR, Capacitive KVAR, CT ratio selected, switching time.

- LED indication for capacitor bank step switched ON, power factor leg/lead shall be provided.

- The Thyristorized switching system shall be inclusive of following facilities.

  - Over voltage protection.

  - Under voltage protection.

  - Over temperature protection.

  - Voltage imbalance protection in each phase.

Facility of manually operating capacitor bank on first in, first out basis.

| MATERIAL DESCRIPTION | APPROVED MAKE |
| --- | --- |
| LT PANELS | CPRI APPROVED PANEL VENDORS |
| LT SWITCHGEARS | SIEMENS , SCHNEIDER |
| LT POWER CONTACTORS | SIEMENS ,SCHNEIDER |
| CAPACITORS | SIEMENS, EPCOS, SUBODHAN |
| THYRISTOR | SIEMENS, EPCOS, SUBODHAN |
| REACTOR | SIEMENS, EPCOS, SUBODHAN |
| RTPFC RELAY | BELUK ,EPCOS , SCHNEIDER |
| PROTECTION RELAY NUMERIC | AREVA ,ALSTOM |
| PROTECTION RELAY ELECTROMAGNETIC TYPE | SCHNEIDER ,AREVA ,ALSTOM, |
| OVERLOAD RELAYS WITH BUILT IN SINGLE PHASE PREVENTER | SCHNEIDER ,AREVA ,ALSTOM ,SIEMENS, |
| PANEL INTERNAL CABLE ,WIRE FRLS TYPE | POLYCAB, FINOLEX, KEI |
| MULTIFUNCTION METER | SIEMENS PAC 3200 , SCHNEIDER- PM 5110 |
| LOAD MANAGER | SIEMENS PAC 4200 , SCHNEIDER- PM 5330 |
| ANALOG METER | RISHAB ,L&T ,AE |
| SURGE PROTECTION DEVICES | OBO BETTERMANN ,SIEMENS , SCHNEIDER |
| SELECTOR SWITCH, TOGGLE SWITCH | SALZER ,KAYCEE |
| TERMINAL BLOCKS | ELMAX , CONNECTWELL |
| PUSH BUTTONS | TEKNIK , SIEMENS ,MOELLER |
| INDICATING LAMPS LED TYPE | SCHNEIDER ,SIEMENS ,TEKNIC |
| SELECTOR SWITCH | RISHAB ,AE ,SECURE |
| ANNOUNCIATOR | MINILEC, PROTON,SCHNEIDER |

Please note: -Combinational major switchgear of different make in panels are not allowed.

ALL THE MATERIAL NOT LISTED ABOVE SHALL HAVE PRIOR APPROVAL FROM THE CLIENT AND CONSULTANT BEFORE PURCHASE / PROCUREMENT.

PACKING AND FORWARDING

SCOPE
This specification covers equipment /material packing transportation and protection of material during transit and storage. 
PACKING: 
Vendor shall be responsible for any damage during transit due to improper or insufficient packing. 
Packing shall be constructed out of sound material and dimensions suitable to the goods, size and weight Fragile material shall be security braced within container or amply fastened to prevent shifting or battering. Cushion lining of appropriate material shall be provided wherever necessary loose material MS parts Nuts bolts etc, shall be packed separately in gunny bags with polythene bags sealed and tagged Components containing glass shall be provided with shock absorbing material cover like thermo Cole. In case of bulk materials Vendor shall supply the same in minimum sub assemblies within the transport limitation Care shall be taken for preventing any seepage of water in case required to prevent any corrosion during transport.
All spare parts shall be separately packed and treated for long storage in site condition. Each crate/package shall contain a packing list in waterproof envelope Vendor/Contractor shall supply any material found short inside the packing at no extra cost. All packing material shall become property of Contractor as the purchaser. All packages shall be clearly, legibly and durably marked on the least two sides.
Destination address: Solapur Sahakari Rugnalaya Niyamit, on F.P. No. 19/2, Pachha Peth, Solapur, Maharashtra 413005.

Dimension and weight: 
Sign showing “ Side up “ with arrow 
Sign “Fragile and Handle with care” for delicate equipment 
Slinging and sling positions 
Important handling and unpacking instructions

Transport: 
No material shall be dispatched without prior consent shipping clearance by the purchaser/ consultant The vendor shall intimate in advance date of dispatch and probable date of delivery at Site so that unloading arrangements can be made, particularly for heavy material in case any equipment is to be transported in sub assemblies or parts, vendor shall furnish all particulars and match marking. Such sub assemblies shall be well within transportation and handling limitations. The transporters shall be provided with proper address and other details, working hours etc. The crate or packages shall be properly secured to avoid movements during transit to minimise possibility of damage.

EXTRA ITEMS AS REQUIRED BY COMPANY: 
The Vendor shall be required to carry out extra items due to Site requirements or changes. The Vendor shall carry out all such items after written consent from the client & consultant both. The Vendor shall submit a rate analysis of these items based on market rates. A margin of 10% shall be allowed over and above the expenses incurred. Escalation shall not be allowed on the extra items. The cost of such extra Item should not exceed than 5% of the contract value.

PAYMENT TERMS:

| STAGES OF PAYMENT | PERCENTAGE AS PER PROJECT COST |
| --- | --- |
| Advance | 30 % |
| Against Performa Invoice before dispatch | 50 % |
| After successful commissioning and testing at site with client and consultant or within 30 days from date of panels reach at site | 15 % |
| Retention for 1 year or PBG for 1 year | 5% |

DEVIATIONS FROM TECHNICAL SPECIFICATIONS

All deviations from technical specifications of contract shall be filled in hereby the bidder.

SECTION			CLAUSE NO.			DEVIATION

The bidder hereby certificates that the above mentioned are only deviations from technical Specifications of this enquiry.

Thanking you,

Yours faithfully,

Seal of Vendor							(Signature of Vendor)