## Sheet1
| BOQ:-SITC of Hydropneumatic System |  |  |  |  | DATE :-17-11-2022
PROJECT :-M/s Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit.
Sr no | Description | Unit | Qty | Supply Rate | Supply Amount | Installation Rate | Installation Amount | Approved Make
1 | Domestic Hydro pneumatic System ( System Capacity of 60 m3 per hour at 40 mtrs head with individual pump capacity of 30 m3per hour )
1.1 | Supply installation testing and commissioning of Hydro - Pneumatic system with 3 nos of Vertical centrifugal pumps ( 1W + 1S + 1 VFD) coupled with Efficiency 1 type motors, with system output of following capacities , 2900 rpm, 3 phase, with suction and discharge headers with individual isolation valves and non-return valves installed on the common base frame, with Hydropnumatic tank of required capacity and the pressure transmitter and PLC controlled Control panel for the hydro-pneumatic system for pumps with cable, water level controller with armoured cable (25mtr), dry run preventer, Single phase preventer, Auto Change over, Volt meter, Ammeter, Auto - Manual switch, ON /OFF & Pump selector switch, as per IP 55 and display. Panel should be PLC controlled with flexibility of taking input to BMS system including the water levels. | nos | 1 |  | 0 |  | 0 | Grundfos / Kirloskar / WILO
2 | Flushing Hydropnumatic System ( System Capacity of 34 m3 per hour at 40 mtrs head with individual pump capacity of 17 m3 per hour )
2.1 | Supply installation testing and commissioning of Hydro - Pneumatic system with 3 nos of Vertical centrifugal pumps ( 1W + 1S + 1 VFD) coupled with Efficiency 1 type motors, with system output of following capacities , 2900 rpm, 3 phase, with suction and discharge headers with individual isolation valves and non-return valves installed on the common base frame, with Hydropnumatic tank of required capacity and the pressure transmitter and PLC controlled Control panel for the hydro-pneumatic system for pumps with cable, water level controller with armoured cable (25mtr), dry run preventer, Single phase preventer, Auto Change over, Volt meter, Ammeter, Auto - Manual switch, ON /OFF & Pump selector switch, as per IP 55 and display. Panel should be PLC controlled with flexibility of taking input to BMS system including the water levels. | nos | 1 |  | 0 |  | 0 | Grundfos / Kirloskar / WILO
| Total |  |  |  | 0 |  | 0
Taxes
| Total Amount with taxes |  |  |  | 0 |  | 0
| Grand Total |  |  |  |  | 0
Mention Payment terms here