## Req. Rate Up to 6th floor
Letter Head
To
Markandeya Rugnalaya
Solapur
Subject: Quotation for Central Medical Gas System up to 6th Floor
Dear Sir,
As per the discussion had with you, reg. below work Ref Rates
Only Fill the Yellow Columns & If at all Any Changes Suggestions Please Mention Or Quote Separtely & Highlight
Sr. No. | Description | Qty. | Unit | Rate | Amount
A | Copper Pipe
1 | Copper Pipe For Medical Use With 42 OD X 1.2 mm for liquid tank to Building duct (Trunch line ) | 220 | met |  | 0
2 | Copper Pipe For Medical Use With 42 OD X 1.2 mm for Oxygen manifold system to Building duct | 100 | met approx |  | 0
3 | Copper Pipe For Medical Use With 42 OD X 1.2 mm | 100 | met |  | 0
4 | Copper Pipe For Medical Use With 35 OD X 1.0/1.2 mm | 400 | met |  | 0
5 | Copper Pipe For Medical Use With 28 OD X 0.9 mm | 650 | met |  | 0
6 | Copper Pipe For Medical Use With 15 OD X 0.7 mm | 3200 | met |  | 0
7 | Copper Pipe For Medical Use With 10 OD X 0.6 mm | 600 | met |  | 0
0
B | Gas Outlets Front Loaded
1 | Oxygen | 288 | Nos. |  | 0
2 | Vacuum | 198 | Nos. |  | 0
3 | Air4 | 89 | Nos. |  | 0
4 | N2O | 0 | Nos. |  | 0
5 | Air7 | 0 | Nos. |  | 0
0
C | Isolation Valves
1 | Isolation valve for 42 mm | 4 | Nos. |  | 0
2 | Isolation valve for 35 mm | 5 | Nos. |  | 0
3 | Isolation valve for 28 mm | 18 | Nos. |  | 0
4 | Isolation valve for 15 mm | 70 | Nos. |  | 0
0
D | Alarm Systems & Valve Box
1 | 4 Gas Microprocessor Alarm with Digital Display | 0 | Nos. |  | 0
2 | 3 Gas Microprocessor Alarm with Digital Display | 7 | Nos. |  | 0
3 | 2-way area valve box | 4 | Nos. |  | 0
4 | 3-way area valve box | 4 | Nos. |  | 0
5 | 5-way area valve box | 0 | Nos. |  | 0
0
E | Oxygen System
1 | Main Oxygen Manifold 8+8 Cylinders With NRV’s Tail pipes etc.. | 1 | Set |  | 0
2 | Oxygen Fully Automatic Control Panel | 1 | Nos. |  | 0
3 | Emergency Oxygen Manifold 4+4 Cylinders With NRV’s Tail pipes & Central Control Regulator | 1 | Set |  | 0
0
F | N2O System
1 | Main N2O Manifold 4+4 Cylinders With NRV’s Tail pipes and Middle frame for cylinder support | 1 | Set |  | 0
2 | N2O Semi Automatic Control Panel | 1 | Nos. |  | 0
3 | Emergency N2O 2+2 manifold System 4 cylinder input supply, Each individual regulator for cylinder, isolation valve for operates one by one cylinder, low presser audio visual indication. | 1 | Set |  | 0
0
G | Air System
1.1 | 30hp Air Oil free Duplex compressors with fully compliant to one of the standards HTM02-01/NEFA/DIN | 2 | nos. |  | 0
OR
1.3 | 30hp Air Scroll compressors with fully compliant to one of the standards HTM02-01/NEFA/DIN | 0 | Rate Only
OR
1.4 | 20hp Air Oil free Duplex compressors with fully compliant to one of the standards HTM02-01/NEFA/DIN | 0 | Rate Only |  | 0
OR
1.5 | 20hp Air Scroll compressors with fully compliant to one of the standards HTM02-01/NEFA/DIN | 0 | Rate Only
2 | Air Receiver Vertical 1000 Lit Capacity | 2 | Nos. |  | 0
3 | 100 CFM Air dryer heatless with2 extra pre filter | 2 | Nos. |  | 0
0
H | Vacuum System
1.1 | 10HP Vacuum Pump oil lubricated with with fully compliant to one of the standards HTM02-01/NEFA/DIN | 3 | Nos. |  | 0
OR
1.2 | 7KW/65CFM Rotary Vacuum Pump with with fully compliant to one of the standards HTM02-01/NEFA/DIN | 0 | Rate Only
2 | Vacuum Receiver Vertical 1000 Lit Capacity | 2 | Nos. |  | 0
3 | Vacuum bactriya & mositure filter | 3 | Nos. |  | 0
0
I | Extra Accessories
1 | Oxygen flow meter BPC with Humidifier | 200 | Nos. |  | 0
2 | Ward Vacuum unit Regulator with 600ml Polycarbonate jar, Tubings | 200 | Nos. |  | 0
3 | Theatre suction unit with 2 X 2000 ml polycarbonate jars. (S.S. Type) | 0 | Nos. |  | 0
4 | O2 Gas outlet probe for flow meter & ventilator | 225 | Nos. |  | 0
5 | Vacuum Gas outlet probe for Vacuum unit | 225 | Nos. |  | 0
6 | Air Gas outlet probe for ventilator& anesthesia | 50 | Nos. |  | 0
7 | Gas outlet installation in bed head panel & pendent | 496 | Nos. approx |  | 0
8 | High pressure tubing | 250 | Met |  | 0
9 | Low pressure tubing | 450 | Met |  | 0
10 | Emergency Oxygen Manifold 3 Cylinders With NRV’s Tail pipes & Central Control Regulator for each floor | 4 | Nos |  | 0
11 | Electic control panel for Air & Vacuum plant | 1 | Nos. |  | 0
0
|  |  |  | Project Cost | 0
|  |  | 18% GST Amt |  | 0
|  |  |  | Total Amount | 0
MGPS STANDARD CRITERIA :
1] Supplier should have ISO-13485 certified company Prefereed
2] The MGPS Supplying Products registered CDSCO certificate
3] Company Profile , Projects in Hand, supplier clients list and Value of Order Executed For MGPS List Need.
4] Copper pipe should be medical grade with Lloyd certified
5] All Quoting Product Model No, Make, Standard Specification Need Seprately
6] Guarantee Period, further AMC / CMC cost For 5 Years Need.
7] All work must need with MGPS Standard and Need All Standatd Documentations.
8]Drawing Preparations And Get Approvals by Supplier
9] Any Core Cut is in suppliers Scope
10] Foundations for plant and electric main Supply at customers Scope
11] any Other Civil Requirement must be informed before along with the Quotations

## Req.Rate for Bed head Panel
Letter Head
To
Markandeya Rugnalaya
Solapur
Subject: Quotation for Bed Head Panel
Dear Sir,
As per the discussion had with you, reg. below work Ref Rates
Only Fill the Yellow Columns & If at all Any Changes Suggestions Please Mention Or Quote Separtely & Highlight
Option : A
Sr. No. | Description | Qty. | Unit | Rate | Amount
A | Bed Head Panel
1 | Aluminum Extruded ICU Bed Head Panel for….. All ICU Approx 6 feet / Pvt & Semi Pvt RoomApprox 3 feet long | 785 | Per feet |  | 0
|  |  | Total Cost |  | 0
|  |  | 18% GST Amt |  | 0
|  |  | Total Amount |  | 0
Option : B
Sr. No. | Description | Qty. | Unit | Rate | Amount
A | Bed Head Panel
1 | Aluminum Extruded ICU Bed Head Panel (Horizontal type) approx 5 to 6 feet Provision for 4 nos. Gas outlets & 8 nos. Electric Switch Socket, Data Point & Nurse Call System Cut Out only with accessories (IV Rod, Basket, Monitor tray & Vacuum Bracket, etc.) for All ICU area | 89 | Nos. |  | 0
2 | Aluminum Extruded Bed Head Panel (Horizontal type) Provision for 2 nos. Gas outlets & 4 nos. Electric Switch Socket , Data Point & Nurse Call System Cut Out only for Private room & semi Private room | 83 | Nos. |  | 0
|  |  | Total cost |  | 0
|  |  | 18% GST Amt |  | 0
|  |  | Total Amount |  | 0
Option : C
Sr. No. | Description | Qty. | Unit | Rate | Amount
A | Bed Head Panel
1 | Aluminum Extruded ICU Bed Head Panel (Vertical type) approx 3 to 4 feet hight & 2feet width Provision for 4 nos. Gas outlets & 8 nos. Electric Switch Socket, Data Point & Nurse Call System Cut Out only with accessories (IV Rod, Basket, Monitor tray & Vacuum Bracket, etc.) for All ICU area | 89 | Nos. |  | 0
|  |  | Total Cost |  | 0
|  |  | 18% GST Amt |  | 0
|  |  | Total Amount |  | 0
MGPS STANDARD CRITERIA :
1] Supplier should have ISO-13485 certified company
2] The BHP Supplying Products registered CDSCO certificate if Applicable
3] Get the Drawings Approvals is Suppliers Scope
4] All Quoting Product Model No, Make, Standard Specification Need.
5] All work must need with Standard and Need All Standatd Documentations.

## Gas Outlet BOQ Up to 6th
MGPS Gas Outlet BOQ up to 6th floor
Area | No.Of Bed | Oxygen | Vacuum | Air4 | N2O | BHP /Pedent | BHP Qty
Basement
MRI | 1 | 1
CT | 1 | 1 | 1
1st floor
Genral Ward-A | 22 | 11 | 11
Genral Ward-B | 28 | 14 | 14
Genral Ward-c | 26 | 13 | 13
2nd floor
Genral ICU-A | 10 | 20 | 10 | 10 |  | BHP 6 ft long | 10
Genral ICU-B | 10 | 20 | 10 | 10 |  | BHP 6 ft long | 10
Semi Pvt.Room | 15 | 15 | 15 |  |  | BHP 3 ft long | 15
Pvt.Room | 1 | 1 | 1 |  |  | BHP 3 ft long | 1
3rd floor
Pvt.Room | 27 | 27 | 27 |  |  | BHP 3 ft long | 27
4th floor
Pvt.Room | 27 | 27 | 27 |  |  | BHP 3 ft long | 27
5th floor
MICU | 12 | 24 | 12 | 12 |  | BHP 6 ft long | 12
SICU | 12 | 24 | 12 | 12 |  | BHP 6 ft long | 12
NICU | 12 | 24 | 12 | 12 |  | BHP 6 ft long | 12
6th floor
MICU | 12 | 24 | 12 | 12 |  | BHP 6 ft long | 12
SICU | 11 | 22 | 11 | 11 |  | BHP 6 ft long | 11
Dialyasis | 10 | 20 | 10 | 10 |  | BHP 6 ft long | 10
Total | 237 | 288 | 198 | 89 |  |  | 159