## BOQ
| BOQ FOR BUSBAR TRUNKING SYSTEM | [6 empty] | VIDYUTSALLAGAR PVT. LTD.
ELECTRICAL CONSULTANT AND ENGINEER
SAVITRI, 113, VINAYAK SOCIETY, SAHAKAR NAGAR NO. 1, PUNE 9.
Email: vidyutsallagar@gmail.com
PHONE 020-24224534
DATE :- 16-06-2021
CLIENT :- M/s Shri Markendey Solapur Sahakari Rugnalaya & Research Center Niyamit.
PROJECT :- Shri Markandeya Solapur Sahakari Rugnalaya
0
SR.NO. | PARTICULARS | QTY | UNIT | MATERIAL RATE | MATERIAL AMOUNT | ERECTION RATE | ERECTION AMOUNT | TOTAL AMOUNT
A | BUSBAR TRUNKING /BUSDUCT
1 | Supply installation testing and commissioning of 300 A SANDWICH TYPE BUSBAR TRUNKING SYSTEM with following specifications & Required all necesory supports. | 61 | MTR. | 0 | 0 | 0 | 0 | 0
THE SPECIFICATIONS FOR THE BBT ARE AS FOLLOWS.
BUS BAR TRUNKING:- IP 54
SHORT CIRCUIT RATING :- 36 KA min
EXPANSION JOINTS SHALL BE PROVIDED.
SYSTEM VOLTAGE:- 1000V
IEC :- 60439-2
CONDUCTOR :- ALUMINIUM
CONDUCTIVITY :- 61%
FIRE RETARDENT PROTECTION CONFIRMING :- IEC 3331/332, NFPA 70
EARTH BUS (EXTERNAL) :- 100%
HOUSING
GALVANISED STEEL SHEET.
THICKNESS:- 2 MM
INSULATION :- CLASS "B'.
INSULATION MATERIAL :- MYLAR OR EPOXY.
SINGLE BOLT BRIDGE TYPE JOINTS.
ALL HARDWARE IN STAIN LESS STEEL WITH HIGHT TENSILE STRENGTH.
BUS BAR SHALL BE TESTED FOR 2.5 KV
VERTICAL SPRING SUPPORT
VERTICAL RIGID SUPPORTS
Straight Length 3 Mtrs With 3 + 3 outlets
a | Flange End | 0 | Nos | 0 | 0 | 0 | 0 | 0
b | Elbow 90 degree standard | 0 | Nos | 0 | 0 | 0 | 0 | 0
c | End Cover | 1 | Nos | 0 | 0 | 0 | 0 | 0
d | Plug Outlet Cover | 24 | Nos | 0 | 0 | 0 | 0 | 0
e | Vertical risers/supports at 2 Meter | 24 | Nos | 0 | 0 | 0 | 0 | 0
f | End Feed Unit with 300A 4P TM MCCB 36kA(min) and WITH CABLE TERMINATION ARRANGEMENT | 1 | Nos | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  | 0
2 | Supply installation testing and commissioning of 100A SANDWICH TYPE BUSBAR TRUNKING SYSTEM with following specifications & Required all necesory supports. | 61 | MTR. | 0 | 0 | 0 | 0 | 0
THE SPECIFICATIONS FOR THE BBT ARE AS FOLLOWS.
BUS BAR TRUNKING:- IP 54
SHORT CIRCUIT RATING :- 25KA min
EXPANSION JOINTS SHALL BE PROVIDED.
SYSTEM VOLTAGE:- 1000V
IEC :- 60439-2
CONDUCTOR :- ALUMINIUM
CONDUCTIVITY :- 61%
FIRE RETARDENT PROTECTION CONFIRMING :- IEC 3331/332, NFPA 70
EARTH BUS (EXTERNAL) :- 100%
HOUSING
GALVANISED STEEL SHEET.
THICKNESS:- 2 MM
INSULATION :- CLASS "B'.
INSULATION MATERIAL :- AIR
SINGLE BOLT BRIDGE TYPE JOINTS.
ALL HARDWARE IN STAIN LESS STEEL WITH HIGHT TENSILE STRENGTH.
BUS BAR SHALL BE TESTED FOR 2.5 KV
VERTICAL SPRING SUPPORT
VERTICAL RIGID SUPPORTS
Straight Length 3 Mtrs With 3 + 3 outlets
a | Flange End | 0 | Nos | 0 | 0 | 0 | 0 | 0
b | Elbow 90 degree standard | 0 | Nos | 0 | 0 | 0 | 0 | 0
c | End Cover | 1 | Nos | 0 | 0 | 0 | 0 | 0
d | Plug Outlet Cover | 12 | Nos | 0 | 0 | 0 | 0 | 0
e | Vertical risers/supports at 2 Meter | 24 | Nos | 0 | 0 | 0 | 0 | 0
f | End Feed Unit with 100A 4P TM MCCB 25kA(min) and WITH CABLE TERMINATION ARRANGEMENT | 1 | Nos | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  | 0
3 | Supply installation testing and commissioning of 32 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs. | 24 | Nos. | 0 | 0 | 0 | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
4 | Supply installation testing and commissioning of 63 A FP MCB Tap of Boxes (IP-54) With Spreder & all required necesory Acessories & supports with MCBs. | 12 | Nos. | 0 | 0 | 0 | 0 | 0
TAP OFF UNITS SHALL BE OF :- IP 54
WITH INTERLOCKING TO AVOID REMOVAL IN POWER ON CONDITION.
| TOTAL OF SECTION A |  |  |  | 0 |  | 0 | 0
SUMMARY OF ElLECTRICAL SITC
A | BUSBAR TRUNKING /BUSDUCT |  |  |  | 0 | 0 | 0 | 0
| TOTAL AMOUNT OF WORK |  |  |  | 0 | 0 | 0 | 0
| GST 18% | [6 empty] | 0
| TOTAL PROJECT COST INCLUSIVE TAXES | [6 empty] | 0